[image: image41.png]INTERLET TOR

AIR INTAKE
o /o
werl, 2
osc
AccumocATON
Fow ose
REGULATORY AccumdcATON
Sevice
T
N eoms

ouTLeT

SAWPLE
POINT.




Sewer System Management Plan

[image: image42.jpg]


City of Colton


[image: image43.jpg]



TABLE OF CONTENTS

1E.0
EXECUTIVE SUMMARY


1E.1
Introduction


2E.2
Elements of the SSMP


3E.3
Regulatory Deadlines


4E.4
Definitions, Acronyms, and Abbreviations


1-11.0
PURPOSE & GOALS


1-11.1
Purpose


1-21.2
Goals


2-12.0
ORGANIZATION


2-12.1
Contact Information


2-12.2
SSMP Team


2-22.3
SSMP Organizational Chart


2-32.4
SSMP Regulatory Deadlines


2-32.5
Roles and Responsibilities


2-42.6
Communications


2-62.7
Sanitary Sewer Overflow (SSO) Reporting


3-13.0
LEGAL AUTHORITY


3-23.1
Compliance Documents


4-14.0
OPERATIONS AND MAINTENANCE PROGRAM


4-14.1
Treatment Facility


4-14.2
Collection System Overview


4-24.3
Collection System Maps


4-64.4
Sewer Cleaning


4-94.5
Manhole Inspection and Assessment


4-94.6
Sewer Lift Stations


4-104.7
Sewer Line Video Inspection (CCTV)


4-104.8
Customer Service Requests


4-114.9
Training


4-114.10
Equipment and Replacement Parts


5-15.0
DESIGN AND PERFORMANCE PROVISIONS


5-15.1
Design Criteria and Standard Construction Design


5-15.2
Sewer Construction Design Review


5-15.3
Staff Involvement in Sewer Construction Plan Review


5-15.4
Testing and Inspection Procedures


5-25.5
City Inspection Personnel


5-25.6
Inflow and Infiltration Manhole Testing


5-25.7
Closed Circuit Television (CCTV) Inspection


5-35.8
Private Sewer Service Lateral Design and Inspection


5-35.9
Standardizations of Equipment and Sewer System Components


6-16.0
OVERFLOW EMERGENCY RESPONSE PLAN


6-26.1
Purpose


6-26.2
Goals and Objectives


6-26.3
Initial SSO Response Procedures


6-36.3.1
Staff Instructions


6-56.3.2
First Responder Duties and Responsibilities


6-56.3.3
SSO Response Field Supervisor


6-56.3.4
Wastewater Reclamation Facility Manager


6-66.3.5
Environmental Compliance Services


6-66.4
Initial Notification Procedures


6-66.4.1
Emergency Call Out Lists


6-106.5
Assessment, Containment, Traffic Control and Clean-up


6-106.5.1
Preliminary Assessment of Damage to Private/Public Property


6-106.5.2
Containment


6-106.5.3
Traffic and Crowd Control


6-116.5.4
Initial Estimates of Flow Volume


6-196.5.5
Additional Measures for Prolonged SSO Conditions


6-196.5.6
Clean-up


6-196.5.7
Monitoring


6-206.6
Private Property SSOs


6-206.7
SSO Reporting


6-216.8
Regulatory Agency Notification Plan


6-216.8.1
Initial Notification


6-246.8.2
Secondary Notification


6-246.8.3
Electronic Reporting Procedures


6-276.8.4
Spill Report Debriefing


6-276.9
Collection System Mapping


6-326.10
Training


6-326.11
Public Advisory Procedure


6-326.11.1
Temporary Signage


6-346.12
SSO Plan Maintenance


6-346.12.1
Submittal and Availability of the SSO Plan


6-346.12.2
Review and Update of SSO Plan


6-346.13
Tracking SSOs


7-17.0
FATS, OILS, AND GREASE CONTROL PROGRAM


7-17.1
Background


7-37.2
FOG Program Elements


7-47.3
Site Inspections


7-67.4
Public Education and Outreach


7-77.4.1
Sample BMP Posters for Food Service Establishments


7-87.4.2
Commercial Grease Interceptor Requirements


7-97.5
Plan Check Inspections


7-107.6
Best Management Practices


7-107.6.1
Food Prep Area BMPs


7-117.6.2
Interceptor and Grease Trap Maintenance BMPs


7-127.7
Sewer Line Cleaning and Assessments


7-137.8
Sewer and Lateral CCTV Inspections


7-137.9
Enforcement


7-147.10
Grease Interceptor Retro Fits


7-167.11
Training


7-167.12
FOG Control Program Summary


7-177.13
Roles and Responsibilities


8-18.0
SYSTEM EVALUATION AND CAPACITY ASSURANCE PLAN


8-18.1
Introduction


8-18.2
Evaluation


8-18.3
Design Criteria


8-28.4
Capacity Enhancement Measures


8-28.5
Plan Updates and Schedules:


8-28.6
Monitoring Capacity Assurance and System Performance


8-38.7
Roles and Responsibilities


9-19.0
MONITORING, MEASUREMENT, AND PLAN MODIFICATIONS


9-19.1
Performance Measures


9-29.2
Baseline Performance


9-29.3
Performance Monitoring and Program Changes


10-110.0
SSMP PROGRAM AUDITS


10-110.1
Audits


10-110.2
SSMP Updates


10-210.3
Annual Goals


10-210.4
Roles and Responsibilities


10-210.5
SSMP Audit Checklist


11-811.0
COMMUNICATION PROGRAM


11-811.1
Direct Mailings, Counter Brochures and Internal Memos


11-811.2
City Web Site


11-811.3
Personal Contact


11-911.4
City’s Call Center


12-112.0
SSMP COMPLETION AND CERTIFICATION


13-113.0
APPENDICES





APPENDICES
Appendix A – Regulatory Permits
  A-1 
Statewide General Waste Discharge Requirements (GWDR)
  A-2 
GWDR Monitoring & Reporting Program
  A-3 
Amended GWDR
  A-4 
San Bernardino County Flood Control MS4 Permit
Appendix B – Notice of Intent
Appendix C – Sewer Use Ordinance Number O-02-15
Appendix D – City of Colton Enforcement Response Plan
Appendix E – City of Colton Sewer Standards
Appendix F – City of Colton SSMP Program Forms
Appendix G – City of Colton Wastewater Master Plan
Appendix H – Capital Improvement Plan (CIP)
Appendix I – Sewer Lateral Policy Ordinance O-02-14
LIST OF FIGURES
2-2Figure 2‑1 Organization Chart


4-3Figure 4‑1 Sewer Line Map Book


4-4Figure 4‑2 Sewer Line Cleaning Map


4-5Figure 4‑3 Sewer Line Video Tracking Map


4-7Figure 4‑4 Sewer Cleaning Log Sheet


5-2Figure 5‑1 Root Intrusion Main Line


5-2Figure 5‑2 Main Line after Cleaning


6-9Figure 6‑1 Sanitary Sewer Overflow Report


6-18Figure 6‑2 Estimating SSO Volume


6-24Figure 6‑3 CIWQS Log-in Screen Shot


6-25Figure 6‑4 SSO Electronic Reporting CIWQS Menu Screen


6-28Figure 6‑5 City of Colton Intranet Utilities


6-29Figure 6‑6 City of Colton Boundary Map


6-30Figure 6‑7 Colton WRF and Incoming Sewer Line Map


6-31Figure 6‑8 Manhole and Sewer Line Map (Partial)


6-33Figure 6‑9 Sewage Spill Sign - English


6-33Figure 6‑10 Sewage Spill Sign - Spanish


6-37Figure 6‑11 SSO Response Flow Chart


7-2Figure 7‑1 Standard Interceptor Drawing


7-4Figure 7‑2 Plugged Interceptor


7-5Figure 7‑3 Main Screen - FOG Control Program


7-7Figure 7‑4 Restaurant FOG Posters


7-9Figure 7‑5 Interceptor Manufacturers, Installers, and Grease Haulers


7-10Figure 7‑6 Interceptor Installation Inspection


7-13Figure 7‑7 Grease Buildup – Sewer Main




LIST OF TABLES

2-1Table 2‑1 Key Personnel & Contact Information


2-3Table 2‑2 Regulatory Deadlines


2-6Table 2‑3 Chain of Communication


4-1Table 4‑1 Conveyance & Pumping


4-2Table 4‑2 Service Area Characteristics


4-2Table 4‑3 Pipe Diameters


4-2Table 4‑4 Pipe Materials


6-4Table 6‑1 Spills Response Duties & Contacts


6-26Table 6‑2 CIWQS Spill Report Summary


6-35Table 6‑3 SSO Summary Report - CIWQS


6-36Table 6‑4 CIWQS No-Spill Summary Report


10-3Table 10‑1 SSMP Audit Categories





E.0
EXECUTIVE SUMMARY
E.1
Introduction

The City of Colton (City) owns and operates the City’s Water Reclamation Facility (WRF).  The wastewater collection system to the City WRF includes 110 miles of gravity sewer mains, 4 miles of force mains, and eight (8) sewer lift stations.  The City WRF accepts wastewater flows from the city of Grand Terrace and from the City of Rialto. The above numbers do not account for the Cities of Grand Terrace or Rialto collection systems. There are interagency agreements that describe the conditions and flow volumes acceptable under the agreement. Please note that the City and Grand Terrace entered into new sewer system agreements in July 2014 that now require the City to operate and maintain Grand Terrace’s sewer collection system.  Additionally, the City is now responsible for responding, mitigating, and reporting of all SSO’s within Grand Terrace area.
On May 2, 2006, the California State Water Resources Control Board adopted Waste Discharge Order (WDR) No. 2006-0003-DWQ, Statewide General Waste Discharge Requirements for Sanitary Sewer Systems (See Appendix A). This Order applies to all federal and state agencies, municipalities, counties, and other public entities that own or operate sanitary sewer systems greater than one mile in length that collect and/or convey untreated or partially treated wastewater to a publicly owned treatment facility in the State of California.

[image: image44.emf]SSO Event 

ID

Spill Start Location 

Name

Agency  Collection 

System

WDID Physical 

Address

Spill Type

Region 

North Rancho 

Avenue

Colton, CA 

92324

300 West 

Hanna Street

Colton, CA 

92324

1988 East Sago 

Palm Street

Colton, CA 

92324

1000 East 

Washington 

Street

C

Colton, CA 

92324

North Mt. 

Vernon Avenue

Colton, CA 

92324

1601 North 

Steel road Road

Colton, CA 

92324

225 West West 

Valley 

Boulevard

Colton, CA 

92324

479 West Casey 

Court

Colton, CA 

92324

479 West Casey 

Court

Colton, CA 

92324

4 64 North 4 th 

Street Alley

Colton, CA 

92324

Category 2 8

647098

00:00.0

400 n 4th 

Street

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636 Category 2 8

647913

00:00.0

479 W. 

Casey

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636

Category 2 8

647915

00:00.0

479 W. 

Casey Ct.

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636 Category 2 8

647918

15:00.0

McDonald's 

restaurant

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636

Category 2 8

653162

40:00.0

1601 Steel 

Road

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636 Category 2 8

653164

00:00.0

Mt. Vernon 

and Fairway

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636

Category 2 8

653168

30:00.0 Shoga Sushi Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636 Category 2 8

710681

10:00.0

1988 Sago 

Palm St.

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636

Category 2 8

714791

00:00.0

Man hole 10-

17 Hanna 

Street

Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636 Category 2 8

725548

55:00.0 Rancho Ave Colton City

Colton Water 

Reclamation 

Facility CS

8SSO10636

 

1-10 of 10

Ensuring proper funding, management, and operations of sanitary sewer systems is one means of achieving the state’s goal of reducing SSOs.  To accomplish this goal, the state is requiring that affected entities develop and implement system-specific Sewer System Management Plans (SSMPs).  These plans will describe measures to provide effective management, operation, and maintenance of sanitary sewer systems.  They will also detail spill response plans to establish standard procedures for proper and effective spill response and reporting.

The SSMP describes all planning, management and operational processes and procedures used that ensure effective management of the sewer collection system.  This document contains existing planning documents (Sewer Master Plan); existing wastewater collection system operational and maintenance procedures; and new programs (i.e., Fats, Oils, and Grease (FOG) Control Program) and procedures necessary that all work toward the common goal of reducing the occurrence and impact of future Sanitary Sewer Overflows (SSOs).  

SSOs are overflows from sanitary sewer systems of domestic, or other, wastewater, and often contain high levels of suspended solids, pathogenic organisms, toxic pollutants, nutrients, oxygen-demanding organic compounds, oil and grease, and other pollutants.  SSOs may pollute surface water or groundwater, threaten public health, adversely affect aquatic life, and impair recreational waters.  WDR 2006-0003-DWQ includes specific requirements related to each agencies responsibility for reducing the number of SSOs and thereby decreasing the risk to human health and the environment caused by such overflows.

WDR No. 2006-0003-DWQ requires all owners of sanitary sewer collection systems to submit a Notice of Intent (NOI) to apply for coverage under this new Order. The City filed for coverage the NOI dated July 27, 2006 (See Appendix B). The City received WDID No. 8SSO10636 from the State Water Resources Control Board, which tracks compliance with electronic SSO spill reporting; SSMP Progress; and Collection System Questionnaire and annual updates.  
The SSO database is maintained through the California Integrated Water Quality System (CWIQS). One element of the Waste discharge Requirements (WDR) is the Sewer System Management Plan (SSMP). The SSMP provides methods for the City to identify, create, and incorporate a multitude of best management practices and procedures to maintain a well functioning collection system. 

The twelve elements of the SSMP consist of existing plans, programs, standards, practices and procedures as well as new programs (e.g. Fats, Oils, and Grease (FOG) Control Program) that were required as conditions of the Statewide General WDR for Sanitary Sewer Systems. The legal authority for implementing the FOG Control Program is contained in the City’s Wastewater Ordinance No. O-02-15 and Chapter 13.08 of the City’s Municipal Code.  All elements of the SSMP considered the following objectives during development: 

1. Improved Customer Service

2. Improved Water Quality and Environmental Protection

3. Long Term Wastewater Collection and Treatment Service

4. Long Term Infrastructure Investment

5. Long Term Financial Stability

6. Workforce Planning and Development

E.2
Elements of the SSMP

The SSMP has twelve elements that must be completed and approved by deadlines listed in Order No. 2006-0003. The mandatory elements of the SSMP are:
1. Goals
2. Organization
3. Legal Authority
4. Operations and Maintenance Programs
5. Design and Performance Standards
6. Overflow Emergency Response Plan
7. Fats, Oils, and Grease (FOG) Control Program
8. System Evaluation and Capacity Assurance Plan
9. Monitoring, Measurement, and Program Modifications 
10. SSMP Program Audits
11. Communication Program

12. SSMP Completion and Certification

E.3
Regulatory Deadlines
The Statewide General WDR contains the following schedule of milestone deadlines:
	Task
	WDR No. 2006-0003-DWQ Section
	Deadline Date

	Development Plan/Schedule

Goals/Organizational Structure
	D 13 (i) and (ii)
	November 2, 2007

	Overflow Emergency Response Program
	D 13 (vi)
	May 2, 2009

	Legal Authority
	D 13 (iii)
	May 2, 2009

	Operations & Maintenance Program
	D 13 (iv)
	May 2, 2009

	Grease Control Program
	D 13 (vii)
	May 2, 2009

	Design & Performance
	D 13 (v)
	August 2, 2009

	System Evaluation & Capacity Assurance Plan
	D 13 (viii)
	August 2, 2009

	Final SSMP
	D 13 (all)
	August 2, 2009


E.4
Definitions, Acronyms, and Abbreviations
Best Management Practices (BMP): Refers to the procedures employed in commercial kitchens to minimize the quantity of grease discharged to the sanitary sewer system. Examples include, but are not limited to, scraping food scraps into a garbage can and dry wiping dishes and utensils prior to washing. 

California Integrated Water Quality System (CIWQS): The State Water Resources Control Board’s online electronic reporting system that is used to report SSOs, certify completion of the SSMP, and provide information on the sanitary sewer system. The electronic reporting requirement became effective on January 2, 2008 in Region 8. 

Capital Improvement Plan (CIP): Refers to the document that identifies future capital improvements to the City’s sanitary sewer system.

Category 1 SS0:  An SSO resulting in a discharge of 1,000 gallons or more; or that results in a discharge to a drainage channel and/or surface water; or to a storm drainpipe that was not fully captured and returned to the sanitary sewer system. 

Category 2 SSO:  All other discharges of sewage resulting from a failure in the sanitary sewer system. 

City: Means the City of Colton. 

Closed Circuit Television (CCTV): Refers to the process and equipment that is used to inspect the condition of gravity sewers. 

County Health: Means the San Bernardino County Department of Health Services.

Environmental Compliance Section: Refers to the City of Colton’s Environmental Compliance Section, which is part of the Water & Wastewater Department. 

Fats, Oils, and Grease (FOG): Refers to fats, oils, and grease typically associated with food preparation and cooking activities that can cause blockages in the sanitary sewer system. 

Food Service Establishment (FSE): Refers to commercial or industrial facilities where food is handled, prepared, or served and where food processing wastewater is discharge to the sanitary sewer system. 

Full-time Equivalent (FTE): Refers to the equivalent of 2,080 paid labor hours per year by a regular, temporary, or contract employee. 

General Waste Discharge Requirements (GWDR): Refers to the State Water Resources Control Board Order No. 2006-0003, Statewide General Waste Discharge Requirements for Sanitary Sewer Systems, dated May 2, 2006. 

Geographical Information System (GIS): Refers to the City’s system that is used to capture, store, analyze, and manage geospatial data associated with the City’s sanitary sewer system assets. 

Global Positioning System (GPS): Refers to a handheld unit or computer program that is capable of producing longitude and latitude coordinates necessary to document the location of sanitary sewer overflows. 

Private Lateral Sewage Discharges:  Sewage discharges caused by blockages or other problems within a privately owned lateral
Sanitary Sewer Overflow (SSO):  A sanitary sewer overflow (SSO) is any overflow, spill, release, discharge or diversion of wastewater from a sanitary sewer system. SSOs include:

· Overflows or releases of wastewater that reach waters of the United States; 

· Overflows or releases of wastewater that do not reach waters of the United States; and

· Wastewater backups into buildings and on private property that are caused by blockages or flow conditions in a sanitary sewer, other than a building lateral.  Wastewater backups into buildings caused by a blockage or other malfunction of a building lateral that is privately owned is a SSO when sewage is discharged off a private property into streets, storm drains, or waters of the State.

Sanitary Sewer System:  Any system of pipes, pump stations, sewer lines, etc., used to collect and convey sewage to a treatment plant.  Temporary storage and conveyance facilities (such as vaults, temporary piping, construction trenches, wet wells, impoundments, tanks, highlights, etc.) are considered part of the sanitary sewer system, and discharges of sewage to these facilities are not sanitary sewer overflows.

Sewage:  Shall mean any liquid waste and water borne solid waste resulting from residential, commercial, industrial, or institutional activities or uses. 

Surface Waters:  All waters of the United States as defined in 40 CFR 122.2 such as navigable waters, rivers, streams, lakes, natural ponds, wetlands, etc.  SSOs to storm drains tributary to surface waters shall be reported as discharges to surface waters.
Abbreviations/Acronyms
AB


Assembly Bill

BAT


Best Available Technology

CFR


Code of Federal Regulations

BMP


Best Management Practices

CAP


Capacity Assurance Plan

CIP


Capital Improvement Program

CM


Corrective Maintenance

CMMS

Computerized Maintenance Management System

CMOM

Capacity, Management, Operations and Maintenance

CWEA


California Water Environment Association

EDU


Equivalent Dwelling Unit

ERP


Enforcement Response Plan

FOG 


Fats, Oils, Grease

GWDR

General Waste Discharge Requirements 

GIS


Geographical Information System

I/I


Inflow/Infiltration

MRP


Monitoring and Reporting Program

NPDES

National Pollution Discharge Elimination System

OERP


Overflow Emergency Response Plan

O&M


Operation and Maintenance

PM


Preventive Maintenance

PVC


Polyvinyl Chloride

RWQCB

Regional Water Quality Control Board

SWRCB

State of California Water Resources Control Board

SSMP 


Sewer System Management Plan

SSO


Sanitary Sewer Overflows

WDR


Waste Discharge Requirements

WWTP

Wastewater Treatment Plant

1.0 PURPOSE & GOALS
The Purpose and Goals for the SSMP stated herein are consistent with the core values adopted by the City. The core values, as adopted by the City Council are:
WE BELIEVE:
“Putting the City First” is the spirit that permeates all deliberations and governs all decisions.

Knowing this gives us the courage to stand up for City issues and manage with financial discipline.
Courage and discipline earn respect.
Sustaining respect requires that we act honestly and deliver with accuracy and timeliness.
Trusted Government will be our legacy.
The City is committed to the goal of developing and implementing a proactive Sewer System Management Plan that reduces the risks associated with sanitary sewer overflows and improves the sustainability and effectiveness of the wastewater collection system. Sewer overflows can pose significant risks to public health & safety; the environment; City workers; public and private property; and the City’s investment in capital infrastructure.  
1.1 Purpose

The purpose of the statewide General Waste Discharge Requirements (GWDR) for Sanitary Sewer Systems is to prevent SSOs. One of the principal components of the GWDR is that each permittee is required to prepare and maintain a Sewer System Management Plan (SSMP) to support the stated purpose. 
The purpose of the SSMP is to protect water quality, eliminate or substantially reduce preventable SSOs, and to protect public health and the environment. The SSMP provides a consolidated document that contains adequate policies, procedures, guidelines, planning documents, programs, and communication requirements that ensure the City properly funds, manages, operates and maintains, all parts of the sewage collection system owned and/or operated by the City. The City will employ adequately trained staff and contractors that posses the necessary knowledge, skills, and abilities to carry out the provisions of this document.
The SSMP provides written guidelines to assist and direct the City in identifying and correcting deficiencies in the wastewater collection system. The main areas of program implementation are sewer line cleaning and video inspection, sanitary sewer overflow (SSO) response and mitigation, agency notification, fats, oils, and grease (FOG) control program to reduce or eliminate the discharge of FOG to the sewer, capital projects to replace and/or repair and expand the sewer collection system, employee training, and public awareness campaigns. 
1.2 Goals
The general goals of the SSMP are:
· To effectively manage, operate, maintain, and improve the City’s wastewater collection system;
· To provide adequate capacity to convey peak flows;
· To provide notifications and reports to all required regulatory agencies in a timely manner;
· To minimize the frequencies of SSOs throughout the City’s collection system;
· To effectively mitigate the effects of any SSO that may occur; and

· To raise awareness of FOG issues, promote Best Management Practices and protect the collection system from FOG related blockages.
To determine the effectiveness of the program and success in meeting the stated general goals, the document contains specific goals and monitoring mechanisms that track progress and provide feedback on performance that allows continued improvements that will maximize SSMP effectiveness.
2.0 ORGANIZATION
This section describes and identifies the City’s SSMP organization and responsible or authorized representatives as required in Section J of SWRCB Order No. 2006-0003. It identifies the administrative, operations and maintenance positions responsible for implementing specific measures in the SSMP with descriptions, responsibilities of personnel, and authority for each position. The Organization element includes a chain of communication for reporting SSOs and line of authority with contact information.   
2.1 Contact Information

Organization’s Name: City of Colton

Address: 1201 S. Rancho
Colton CA 92324
2.2 SSMP Team
The following Table lists key personnel and contact information:
Table 2‑1 Key Personnel & Contact Information
	Positions
	Office Phone 

No. 
	Cellular

Phone No.

	City Manager
	(909) 370-5051
	

	Public Works Director
	(909) 370-6199
	

	Public Works Inspector
	(909) 370-6128
	(951) 515-0274

	Wastewater Reclamation Facility Manager
	(909) 370-5599
	(909) 772-7895

	Wastewater Maintenance
	(909) 370-6142
	(909) 772-3480

	FOG Control Program Inspector
	(909) 370-6128
	(951) 515-0274

	Regulatory Compliance 
	(909) 370-6128
	(951) 858-1542

	Collection System Maintenance
	(909) 370-5190
	(909) 821-8940

	After Hours Emergency Contact
	(909) 370-5000
	Emergency 911

	
	
	


2.3 SSMP Organizational Chart

[image: image1.jpg]City of Colton
Sewer System Management Plan

Organization Chart

City Council

Legal
Counsel

I

City Manager

Public Works

City Engineer Director

!—I—|

Associate Project [
Engineer
a Manager Veastowdtar Utilties
Reclamation
Inspector
Manager
Public Works i~ ” "Environmental ~ T Collection
Inspector i Compliance Department | Systems
| Facilty Inspections | Maintenance

i I
! FOG Control iSpill Prevention &

i _____ Vf‘—\

Program | Containment |





Figure 2‑1 Organization Chart
[image: image45.png]CY°'°§('°"0LColton




2.4 SSMP Regulatory Deadlines 
	Task
	WDR No. 2006-0003-DWQ Section
	Completion Deadline

	Development Plan/Schedule Goals/Organizational Structure
	D 13 (i) and (ii)


	November 1, 2007

	Overflow Emergency Response Program
	D 13 (vi)
	May 1, 2009

	Legal Authority
	D 13 (iii)
	May 1, 2009

	Operations & Maintenance Program
	D 13 (iv)
	May 1, 2009

	FOG Control Program
	D 13 (vii)
	May 1, 2009

	Design & Performance
	D 13 (v)
	August 1, 2009

	System Evaluation & Capacity Assurance Plan
	D 13 (viii)
	August 1, 2009

	Final SSMP
	D 13 (all)
	August 1, 2009


Table 2‑2 Regulatory Deadlines

2.5 Roles and Responsibilities

City Manager - Establishes policy, plans organizes, and directs the activities of the Public Works Director.  Reviews budgets and recommends financing related to wastewater system infrastructure. Reports and advises the City Council regarding financial impacts of city and regulatory programs on the citizens and businesses within the City. 
Public Works Director - Under general policy direction, plans organizes, directs and implements comprehensive strategies and programs for the operation of a large potable water distribution and wastewater collection and treatment system. Manages and coordinates all aspects of the City’s Operations Department and assists in coordinating the development and implementation of SSMP. 
Director of Engineering - Under general policy direction, plans, organizes, directs and implements the City’s engineering activities and operations. Prepares wastewater collection system planning documents, manages capital improvement delivery system, documents new and rehabilitated assets and assists in coordinating the development and implementation of SSMP.
Wastewater Reclamation Facility Manager – Under the general direction of the Director of Operations, plans, organizes, directs and administers the operations and maintenance of the City’s wastewater and reclaimed water facilities and Preventive Maintenance functions. The Wastewater operations manger also coordinates the development and implementation of the SSMP.

Collection System Maintenance - Assists in coordinating the development and implementation of the City’s SSMP. Manages field operations and maintenance activities, provides relevant information to agency management, prepares and implements contingency plans, leads emergency response, investigates and reports SSOs and trains field crews. Supervises the operation, maintenance, and cleaning of lift stations domestic sewer systems and contract wastewater systems.
Environmental Conveyance Staff (or Contractors) - Performs a wide variety of preventive maintenance activities, mobilizes and responds to notification of stoppages and SSOs (mobilize sewer cleaning equipment, by-pass pumping equipment, and portable generators). Perform routine sewer line cleaning, inspects, and reports activities to the Wastewater Reclamation Facility Manager. 
Public Works Inspector - Ensures that new and rehabilitated assets meet City standards, works with field crews to handle emergencies when contractors are involved, provides verbal reports to Principal Engineer of Construction Management.
Environmental Compliance Department (contracted) – Manages and assists in administering the City’s approved Pretreatment Program. Assist the City in complying with Federal, State and local environmental laws and regulations. Develop and prepare as needed on applicable permits, conduct inspections at industrial user facilities and provides support to all elements of City’s SSMP.    

Note:  Job descriptions for the positions listed in the organizational charts are available from the Human Resources Department. Primary responsibility for the day-to-day management and O&M of the collection facility assets resides within the Water and Wastewater Department. The Wastewater Reclamation Facility Manager manages the daily field activities.
2.6 Communications
The reporting of SSOs is detailed in Section 6 - Overflow Emergency Response Plan. A copy of the SSO response is maintained by the City’s Wastewater Department located at 1201 S. Rancho, Colton CA 92324. The following items are included in the document:
· List of regulators, individuals, agencies, and public stakeholders to be notified if there is a potential exposure to SSO pollutants;

· Name, title, phone, and location of the person reporting SSO’s to the OES, OCHCA, and RWQCB;

· List of records maintained in support of SSO reporting;
· Policies and procedures that identify roles and responsibilities, documentation requirements, and the process for collecting and retaining SSO records;

· Procedure for immediate notification of SSO’s to the RWQCB;

· Procedure for reporting overflows to storm drains and tributaries to Waters of the United States;

· Procedures for reporting overflows of 1,000 gallons or greater to the OES; 

· Procedures for submitting electronic SSO reports;
· Procedures, roles, and responsibilities for personnel responsible for completing the SSO report forms and forwarding them to the RWQCB;

· Procedure, roles, and responsibilities for developing and submitting monthly reports; and

· Procedures for submitting no-spill certification reports. 
2.7 Sanitary Sewer Overflow (SSO) Reporting

Specific SSO response procedures are covered in Section 6 of this document – Overflow Emergency Response Program.  The chain of communication for reporting SSOs is as follows:

	Staff
	Responsibility

	First Responder
	· Provide initial evaluation of spill severity

· Call emergency services, as required

· Notify Spill Response Supervisor

· Stop spill and secure area as instructed by Spill Response Supervisor

	Spill Response Supervisor (Wastewater Reclamation Facility Manager)
	· Direct First Responder in initial actions to control spill and prevent public exposures to spill

· Evaluate spill and determine actions to control and cleanup  

· Notify Public Works Director
· Mobilize City personnel/equipment to respond to spill

· Contact and direct outside services, as required, to respond to spill

· Review Field Logs and Complete Reports as determined by review.  

· Provide agency notifications as required:

· RWQCB

· Riverside County Department of Environmental Health

· CA Office of Emergency Services
· SWRCB

	Pretreatment Services
	· Determine required sampling for spill.

· Assist with regulatory reporting as directed.

· Investigate Potential Commercial/Industrial Sources

	Public Works Director
	· Authorize City resources to respond to spill

· Communicate with City Manager, Public Information Department, and others as required

	Legally Responsible Official (LRO)
	· Submit Certified regulatory spill reports electronically through CIWQS


Table 2‑3 Chain of Communication
The individual with primary responsibility for ensuring adequate response to SSOs during normal business hours is the Wastewater Operations Manager. On weekends and after hours the primary responsibility for response to SSOs is assigned to call personnel.
3.0 LEGAL AUTHORITY

This Section describes how the City’s legal authority addresses those mandatory SSMP provisions outlined in Section D, 13 (iii) Legal Authority of SWRCB Order no. 2006-0003.
The City has sufficient legal authority contained in several documents and codes that enable designated personnel to protect the collection system against harmful wastewater discharges or activities, storm water infiltration and inflows (I/I). City adopted standards, policies are used to ensure sewers, sewer appurtenances, and lateral connections are properly designed and constructed. The following is a discussion of those documents.

· Ordinance No. O-02-15 Section II prohibits illicit discharges from entering into the City’s sewer system, which may cause or contribute to interference with normal operations.  The Ordinance is codified in Chapter 13.08 of the City’s Municipal Code. This section contains specific prohibitions against the discharge of any material or waste that could harm the collection system, wastewater treatment plant or jeopardize the safety of the City’s collection system personnel. 
· Sewer lines and sewer connections are required to meet the criteria contained in the Greenbook: Standard Specifications for Construction & Standard Drawings for Water & Sewer Facilities, and the latest City approved edition of the Uniform Plumbing Code.
· The City has sewer easements in place to ensure access for maintenance, inspection, or repairs for portions of the lateral owned or maintained by the City. The City has a variety of methods for obtaining easements to construct and maintain sewer lines through private property:

1. Acquisition of the easement through voluntary purchase from the owner

2. Acquisition through condemnation for a sewer line easement.

3. As a condition of development, the property owner is requested to dedicate or grant an easement to the City for sewer line installation.

These easements permit the City to conduct periodic and scheduled sewer line cleaning to prevent SSO’s.
If the City is unable to obtain an easement or prevented from accessing the property to perform routine maintenance and a problem arises with the sewer line, the City could request assistance from San Bernardino County Department of Health if the situation (lack of adequate sewer services) renders the property uninhabitable. 
City Ordinance No. O-02-15 Section II has several sections that prohibit or limit the discharge of fats, oils, greases and other debris that may cause blockages. These sections are:

1. 13.08.210 General Discharge Prohibitions
2. 13.08.211 Specific Discharge Prohibitions
3. 13.08.215 Prohibition Against Discharging Solid or Fluid Material to Watercourses
4. 13.08.222 Point of Discharge Limits
The City has the authority to restrict or prohibit the discharge of storm water into the collection system. This authority is granted through Ordinance No. O-02-15 Section II,13.08.211- Specific Discharge Prohibitions.
The City’s has administrative and administrative penalty provisions in the Municipal Code Section 13.08 to seek actions against any user found in violation of Ordinance No. O-02-15 and any permits or control documents issued pursuant to Ordinance No. O-02-15 Section III. 

The City uses an Enforcement Response Plan, as part of the Pretreatment Program, for guidance in the implementation of enforcement actions for violations of Ordinance No. O-02-15 Section IV
3.1 Compliance Documents

The legal authority for enacting the SSMP programs and policies are included in the following documents: 

· Sewer Use Ordinance No. O-02-15 (Appendix C)
· Enforcement Response Plan (ERP) (Appendix D)
· Fats Oils and Grease (FOG) Control Program (Section 7)
· Standards & Specifications (Appendix E)
4.0 OPERATIONS AND MAINTENANCE PROGRAM
The City’s Operating and Maintenance Program addresses those mandatory SSMP provisions outlined in Section D, 13 (iv) Operation and Maintenance Program of SWRCB Order No. 2006-0003. This Section describes the City’s measures and activities regarding operations and maintenance, management of engineering data, capacity assurance, training programs, and communication programs.

4.1 Treatment Facility

The City owns and operates one wastewater treatment plant (hereinafter referred to as a Publicly Owned Treatment Works (POTW), with the following specifications:

A. Facility Design capacity = 10.4 MGD 

B. Average Daily Flow = 5.4 MGD 

C. Average Dry Weather Flow = 5.4 MGD
4.2 Collection System Overview
The City is responsible for the maintenance of approximately 114 miles of sewer line.  The City contracts with a private sewer line cleaning company for all routine cleaning services.  The City cleans the entire 114 miles of sewer system annually.  There are no combined storm/sanitary sewers within Colton’s jurisdiction.  Table 4-1 indicates the age of the collection system components and the relative percentage of each component within a specific age category. The information below indicates that 70 % of the City’s sewer collection system is more than 50 years old. 
Table 4‑1 Conveyance & Pumping
	Year Built
	% of Total

	
	Gravity Sewers
	Pump Stations

	2000 – present
	2
	12.5

	1980 – 1999
	18
	25

	1960 – 1979
	10
	25

	1940 – 1959
	60
	25

	1920-1939
	10
	12.5


Table 4‑2 Service Area Characteristics
	Characteristic
	Quantity

	Service Area (City of Colton Boundaries)
	18 square miles

	Population
	51,781

	Annual Average Precipitation
	16.43 inches

	Residential Sewer Connections
	13,643

	Commercial/Industrial Sewer Connections
	734

	Municipal Connections
	40


Table 4‑3 Pipe Diameters
	Pipe Diameter
	Gravity Sewers %
	Gravity Sewer Miles
	Force Mains %
	Force Main Miles

	8 inches or less
	70%
	48.79
	47%
	8.77

	9 -18 inches
	26%
	18.54
	53%
	10

	19 – 36 inches
	4%
	2.77
	0
	0

	> 36 inches
	0
	0
	0
	0

	Totals:
	
	70.1
	
	18.77


Table 4‑4 Pipe Materials
	Pipe Diameter
	Gravity Sewers %
	Force Mains %

	Polyvinyl Chloride Plastic
	10%
	70%

	Vitrified Clay Pipe (VCP)
	70%
	

	Concrete
	20%
	

	Asbestos  Concrete
	
	15%

	Ductile Iron
	>1%
	15%


The proposed Wastewater Department operations and maintenance budget for FY08/09 was $10,432,018 with approximately $2,000,000 set aside for capital improvements.  
4.3 Collection System Maps
System mapping is a means to provide access to sewer plans, drawings, and electronic records. The following graphics illustrate several of the mapping strategies employed by the City to track cleaning activities, CCTV activities, and pipeline configurations.

[image: image2.jpg]CITY OF COLTON
MAP BOOK

PUBLIC UTILITIES
FIRE & GIS





[image: image3.jpg]



Figure 4‑1 Sewer Line Map Book

Wastewater staff utilizes information from the Public Utilities map book on a daily basis. Valuable information regarding line size, configuration, lift stations, etc. is used in the day-to-day decision making regarding sewer line issues. 
The City also tracks progress with line cleaning and video tasking on maps located in the wastewater operations trailer. See Figures 4-2 and 4-3. 

[image: image4.jpg]



Figure 4‑2 Sewer Line Cleaning Map
[image: image5.jpg]



Figure 4‑3 Sewer Line Video Tracking Map
Section 6.16 includes detailed information on the types and available of all sewer collection system maps.
All manholes have a unique identifying number on the GIS and the sewer lines between manholes are identified by pipe size and material, length between manholes and upper and lower elevations.

4.4 Sewer Cleaning
The City’s Wastewater Department contracts a variety of sewer cleaning activities to ensure the reliability of the City’s sewer collection system. The current goal is to have the City’s entire sewer collection system cleaned every year. Progress with this goal is tracked by weekly meetings with the contractor, updating the wall map (Figure 4-2) updating the Excel Spreadsheet that track area cleaned, notes any problems, calculates total feet cleaned to date, CCTV footages, etc.  See Figure 4-4, which shows a sample spreadsheet.  
[image: image6.emf]TTL FT CLEANED                                 TOTAL VIDEO  

0

 Date

FROM 

MH #

TO MH #

LINE 

SIZE

FEET STREET CROSS STREET LINE CONDITIONS CLEANED BY VIDEO

01/07/08 10-29 10-29A 8" 122 4Th St F St Line needs video City

01/08/08 25-34 25-36 18" Easement(Walmart) H&H

01/08/08 25-15 25-16 10" 250 Santo Antonio Dr H&H

01/08/08 25-13 25-14 18" 400 Mt Vernon Ave Heavy Grit H&H

01/08/08 25-18 25-15 18" 50 Mt Vernon Ave Grit-Vacuumed H&H

01/08/08 25-19 25-18 18" 400 Mt Vernon Ave Grit-Vacuumed H&H

01/08/08 25-20 25-19 Medium Grit H&H

01/08/08 25-20 25-21 10" 257 Centerpoint Dr Light Grit H&H

01/08/08 25-27 25-26 18" 400 Mt Vernon Ave Light Grit H&H

01/08/08 25-27 25-34 24" 340 Easement(Walmart) Medium Grit H&H

01/08/08 25-26 25-20 18" 30 Mt Vernon Ave Light Grit H&H

01/08/08 25-33 25-27 27" 87 Washington St Medium Grit H&H

01/08/08 25-32 25-33 24" 315 Washington St Medium Grit H&H

01/08/08 25-31 25-32 24" 325 Washington St Light Grit H&H

01/09/08 25-30 25-31 24" 325 Washington St Medium Grit H&H

01/09/08 25-29 25-30 24" 310 Washington St Medium Grit H&H

01/09/08 25-28 25-29 24" 70 Washington St Medium Grit H&H

01/09/08 29-17 25-28 24" 385 Washington St Medium Grit H&H

01/09/08 24-52 24-51 10" 205 Easement(cttnwd) Medium Grit H&H

01/09/08 24-53 24-52 10" 275 Easement(cttnwd) Medium Grit H&H

01/09/08 24-54 24-53 10" 320 Easement(cttnwd) Medium Grit-Vacuumed H&H

01/09/08 24-55 24-54 10" 330 Easement(cttnwd) Medium Grit-not Vacuumed H&H

01/09/08 29-18 30-71 10" 302 Easement(RedTile) Medium Grit & Rocks H&H

01/09/08 29-19 29-18 10" 380 Easement(Pointapt) Medium Grit & Grease   H&H

01/09/08 29-20 29-19 10" 310 Easement(Pointapt) Medium Grit & Grease Vaccd H&H

01/09/08 29-22 29-20 10" 672 Easement(Pointapt) MH 29-21 is Buried H&H

01/10/08 29-14 29-16 24" 755 Washington St Med.,Grit, Vacuumed H&H

01/10/08 29-13 29-14 24" 380 Washington St Med.,Grit, Rocks, Vacuumed H&H

01/10/08 29-12 29-13 24" 380 Washington St Med., Grit, Vacuumed H&H

01/10/08 29-11 29-12 24" 370 Washington St Medium Grit H&H

01/10/08 29-30 29-31 8" 230 Mediterranian Pkwy Medium grit H&H

01/10/08 29-29 29-30 8" 140 Mediterranian Pkwy Medium Grit H&H

01/10/08 29-28 29-29 10" 110 Mediterranian Pkwy Medium Grit, Vacuumed H&H

01/10/08 29-27 29-28 10" 30 Mediterranian Pkwy Medium Grit, Vacuumed H&H

01/10/08 29-26 29-27 10" 107 Milano Way Medium Grit H&H

01/10/08 29-27 29-25 10" 200 Milano Way Medium Grit, Vacuumed H&H

01/10/08 29-24 29-25 10" 282 Milano Way Medium Grit, Vacuumed H&H

01/10/08 29-23 29-24 10" 189 Del Sol Medium Grit H&H

01/10/08 29-11 29-23 10" 226 Del Sol Medium Grit, Vacuumed H&H

01/11/08 29-16 Washington St Rv Center Dr Located MH City

01/14/08 6-114 6-115 8" 380 Olive St Mt Vernon Ave Grease, Gritt City

01/14/08 25-77 Rancho St  Agua Mansa Rd MH Cleaned Out(Hot Spot) City

01/15/08 6-105 6-104 8" 175 Citrus St Mt Vernon Ave Gritt, Grease(Hot Spot) City

01/16/08 3-24 3-25 8" 400 Johnston St Pennsylvania Ave Gritt, Grease(Hot Spot) City

01/16/08 15-2 15-3 8" 500 Fairway Dr Mt Vernon Ave Gritt, Grease, Rags(Hot Spot) City

01/22/08 29-10 29-11 24" Washington St No Access H&H

01/22/08 29-9 29-10 24" 370 Ease.Santa Ana Rv Light Debris H&H

01/22/08 29-8 29-9 24" 380 Ease.Santa Ana Rv Light Debris H&H

01/22/08 29-7 29-8 24" 365 Ease.Santa Ana Rv Light Debris H&H

01/22/08 29-6 29-7 24" 370 Ease.Santa Ana Rv Light Debris H&H

01/22/08 29-5 29-6 24" Ease.Santa Ana Rv No Access, MH Buried H&H

01/22/08 29-4 29-5 24" 288 Ease.Santa Ana Rv Medium Debris H&H

01/22/08 29-3 29-4 24" 386 Ease.Santa Ana Rv Medium Debris H&H

01/22/08 29-2 29-3 24" 385 Ease.Santa Ana Rv Medium Debris H&H

01/29/08 28-10 8" Terrace Ave la Cadena Dr Located MH City

01/29/08 28-12 8" Terrace Ave la Cadena Dr Located MH City

01/29/08 28-13 8" Terrace Ave la Cadena Dr Located MH City

01/29/08 29-1 8" Alston Ave la Cadena Dr Located MH City

01/29/08 2-49 8" Alston Ave Citrus St Located MH City

01/29/08 2-48 8" Terrace Ave Citrus St Located MH City

01/30/08 29-1 28-11 8" 344 Terrace Ave la Cadena Dr Gritt, Rocks, Grease City

01/30/08 2-48 2-47 8" 410 Alston Ave Citrus St Gritt, Rocks, Grease City

01/30/08 2-53 2-48 8" 820 Citrus St Alston Ave Gritt, Rocks, Grease City

01/30/08 35-52 35-53 8" 280 Terrace Ave H&H

01/30/08 35-51 8" 280 Terrace Ave H&H

01/30/08 35-50 8" 50 Terrace Ave H&H

01/30/08 Extra Lid 8" 300 Terrace Ave H&H

01/30/08 35-49 35-50 8" 280 Terrace Ave H&H

01/30/08 35-48 35-49 8" 252 Terrace Ave H&H

2008

916,022

COLLECTION MAINTENANCE LOG


Figure 4‑4 Sewer Cleaning Log Sheet
The Water & Wastewater Department also tracks the following: 
A. Routine cleaning

B. Preventative cleaning and maintenance

C. Repairs

D. High frequency cleaning and maintenance

E. Roach control

F. CCTV (Routine and new lines for acceptance)
A manual scheduling work order system is used to generate the work orders for sewer line cleaning. The scheduled cleaning is based upon the date last cleaned. The goal is to have the entire sewer system cleaned every 12 months so the last cleaned date is typically 12 months prior to the current date. The last cleaned date could also change depending upon need based cleaning, e.g. to remove a blockage. At the beginning of each week, the collection crew is informed regarding the lines that require servicing during that week.  When a section of the sewer is cleaned, the collection crew completes a cleaning record of that section of sewer including:

· Date and time of the cleaning

· Method of cleaning
· Identity of the cleaning personnel

· Cause of any stoppages

· Location of stoppage or routine cleaning activity

· Any further actions that are necessary or taken

When the job is completed, the collection crew writes their findings on the work order and all the completed work orders are returned at the end of the day with the statistics for the day. (e.g., sewer line footage cleaned; CCTV footage; etc.) The information contained in the work orders are entered into the sewer maintenance log. Trends can be identified for a wide variety of sewer problems, e.g. roots, grease accumulations, hydraulic restrictions and surcharge conditions. The information from the work orders also determines if an area is in need of high frequency cleaning due to periodic obstructions, e.g. roots, grease.

One of the primary goals of the SSMP is to reduce the number of sanitary sewer overflows (SSO’s). The Operations-Wastewater department has several activities and programs that contribute to the reduction of SSO’s:

· A sewer inspection program is being developed that will document chronic sewer problems and makes recommendations for increased cleaning frequencies for problematic areas. Additionally, the source(s) of the chronic sewer problem(s) will also be determined and addressed. These problematic sites are added to the high frequency cleaning list until effective mitigation of the problem is accomplished.
· The City has a Fats, Oil, and Grease (FOG) program to prevent excessive accumulations of FOG that can lead to SSO’s. On-site interceptor inspections, education regarding best management practices, and the Collection System’s CCTV program, which is used to document and prioritize FOG Control Program efforts before actual SSOs occur.
· SSO’s are plotted based upon geographical location noted by address, if possible. The sewer line affected is provided and the cause of the blockage is provided.

4.5 Manhole Inspection and Assessment

The City’s Wastewater Department and contractors also inspect manholes as part of the cleaning activities. If deficiencies are found, then a work order is created to correct the problem. There is no set goal for the inspection of manholes and there is no grouting program. When the manholes and the sewer lines are inspected, the following observations are recorded:

· Conditions of the manhole frame and cover

· Evidence of surcharge 

· Offsets or misalignments

· Details of the primary cause of cracks or breaks in the manhole or pipe, including blockages

· Presence of corrosion (only if extreme)

· If repairs are necessary

· Manhole identifying number and location

· Wastewater flow only if surcharged or backed up

· Presence of infiltration, location, and estimated quantity

· Accumulations of grease, debris, or grit

4.6 Sewer Lift Stations
The City has eight (8) sewer lift stations. Work is progressing on the development of a Standard Operating Procedures manual for each station, including emergency procedures. All sewer lift stations have telemetry for communication with the POTW to indicate high wet well conditions. In the event that power is lost and the station(s) cannot pump the wastewater, City combination (water jetter/suction) trucks and/or contacted pumping companies are called to pump the station(s) wet well until the station can become operational. 
The height of the wet well engages pump operations to either cycle on (at high levels) or cycle off (at low levels). Lift stations contain built-in redundancy to improve system reliability. Pumps are rotated in the lead and lag positions to ensure operation integrity. Should the second pump be required for operation, the station electronically will engage the second pump. Pump stations are equipped with electrical connections for portable stand-by generators. Riverside pump station has a permanent stand-by generator. All pump stations have radio telemetry for high-level alarm status. The plants SCADA system is capable of sending a telephone notification of alarms to on call staff during after hours.
All sewage lift stations are inspected bi-weekly. Operations logs are kept for all of the stations.
4.7 Sewer Line Video Inspection (CCTV)

The City’s closed circuit television (CCTV) inspection crew perform video inspections of City sewer lines and private development sewer lines. The City crews are trained in the use of the equipment. The video inspections address the following:
· Pipe size, type, length, and joint spacing

· Distances are recorded

· Structural deficiencies

· Corrosion

· Inflow/Infiltration

· Illegal connections

· Results of the video inspection

· CCTV operator name

· Cleanliness of the line

· Location and identification of the line and manholes being examined

Once the CCTV examination is completed, the sewer line rated based upon the defects discovered during the video examination. The City recognizes that the CCTV program is vital in the effective management and maintenance of the sewer collection system.
4.8 Customer Service Requests

As part of the customer service program, the Wastewater department personnel accept service requests from City customers. These service requests describe sewer problems the customer is having or has observed. These problems could be related to the homeowner’s private lateral, foul odors, or problems with a sewer line. When a service request call is received, a service request form is complete; this form includes the following information:

· City personnel who received the complaint or request

· Nature of the complaint or request

· To whom the follow-up action was assigned

· Date of the complaint or request

· Date the complaint or request was resolved

· Name, address, and telephone number of the complainant or requestor

· Location of the complaint or request

· Date the follow-up action was assigned

· Cause of the problem

· Investigation findings

· Corrective actions taken

In most all cases, the outdoor exposed impervious surface areas that were contaminated with sewage are contained and washed down and the wastewater is removed by a City combination truck. The Operations-Wastewater department personnel respond as soon as the call is received during working hours and after hours, the standby crew is in route to the treatment plant within sixty minutes of notification. The goal for resolution of each service request is to have all matters related to the service request concluded by the day’s end. 

4.9 Training

The City uses the California Water Resources Control Board mandatory certification program for wastewater operators and collection crew. The City requires the possession of a voluntary certification obtained from the California Water Environment Association (CWEA) for many positions in the Operations-Wastewater department. These certifications are for entry level to management. The certification is available in a variety of disciplines, in addition to wastewater.

All employees in the Wastewater department are evaluated annually for performance. On-the-job-training is critical for many specific activities of some positions in the Operations-Wastewater department. Specifically, the collection system personnel receive on-the-job-training for the use of various kinds of sewer cleaning equipment and devices. Demonstrations, drills, and periodic testing are used to evaluate the skill sets of the employees.
4.10 Equipment and Replacement Parts

The Wastewater department collection has one vehicles for the care and maintenance of the sewer system. One high-pressure hydro trucks has sewer line cleaning capabilities. One CCTV van has the ability to video inspect laterals and sewer lines up to six inches. This van is equipped with all the necessary video equipment to create the sewer video. 

The Operations-Wastewater department maintains some of the expendable parts for the hydrovac trucks. These parts include nozzles and root cutters. Each vehicle receives routine preventive maintenance by City staff.
Major repairs are contracted on an as need basis.

5.0 DESIGN AND PERFORMANCE PROVISIONS
This section addresses SSMP provisions outlined in Section D, 13 (v) Design and Performance Provisions of SWRCB Order No 2006-0003 and references the design and construction standards & specifications that the City uses for new sewer systems, pump stations, and other appurtenances, and for the rehabilitation and repair of existing sewer systems. Also included are the procedures and standards for the inspection and testing of these facilities.

The Public Works Director develops and approves water and wastewater utility standards for the Department.  The Director is also responsible for prioritizing capital sewer projects that include the repair, replacement, and installation of new sewer line(s) and sewage lift stations. 

5.1 Design Criteria and Standard Construction Design

The City uses two primary resources to design and review sewer construction drawings. These are:

A. Standard Drawings for sewer line construction (Appendix E)
B. Greenbook Standard Specifications for Public Works Construction, latest edition.
5.2 Sewer Construction Design Review
The City’s Standard Drawings and the Greenbook are used to review sewer construction blueprints. 

5.3 Staff Involvement in Sewer Construction Plan Review

The City’s Water & Wastewater Division includes a Utility Inspector and Utilities Engineer that review plans for all new sewer projects. Plans must comply with established standards and on-site inspections verify installations comply with approved standards and plans.  
5.4 Testing and Inspection Procedures

The City follows Greenbook, Section 306, Underground Conduit Construction procedures for inspecting and testing new and rehabilitated sewer projects, during and after construction. The City has adopted written general sewer requirements that accompany each set of approved plans that include but are not limited to construction requirements, regulatory requirements, video confirmation of connections, line cleaning to ensure no debris remains in the lines, etc.
5.5 City Inspection Personnel

The Utilities Engineer reviews all sewer plans for compliance with established standards. Once approved, the City’s Water & Wastewater Department Utility Inspector inspects all sewer line installations from the property line to the connection point on the main sewer line. The City Building Department and the Environmental Compliance Section (Water & Wastewater Department) review, approve, and inspect on-site (from the property line into the facility) commercial plumbing for compliance with plumbing codes and Pretreatment Program requirements. 
5.6 Inflow and Infiltration Manhole Testing

The new manholes are visually tested to determine if there are any conditions of inflow or infiltration and to ensure that all connections are in accordance with standards. This activity is particularly important in areas with traditionally shallow groundwater tables and if groundwater is detected in the construction trenches during the project life.

5.7 Closed Circuit Television (CCTV) Inspection
[image: image46.jpg]


The Public Works Department – Wastewater Division has a collection maintenance unit which includes 1 crew (4 employees) responsible for the maintenance and CCTV of the sewer system. CCTV is required for all new sewer tie-ins to ensure proper connections and clear lines prior to use. CCTV is used in conjunction with the maintenance program on existing sewer lines to help isolate problems and to establish clear priorities for the maintenance needs in the sewer collection system. The video inspection also detects “sags” in the line and other problematic conditions 
[image: image47.jpg]


Figure 5‑1 Root Intrusion Main Line 

that require attention.  CCTV is also useful when responding to customer complaints
about “slow draining” sewers.  The video captures shown below show main line infiltrated by roots from a private sewer lateral (Fig. 5-1) and after cleaning the main line (Fig 5-2). 
   Figure 5‑2 Main Line after Cleaning

5.8 Private Sewer Service Lateral Design and Inspection

The City uses the Greenbook, Standard drawings, and the Uniform Plumbing Code to detail the specifications and construction for private sewer lateral design and construction. The Water & Wastewater Department Utilities Engineer and Utilities Inspector review and approve sewer drawings. Per sewer lateral ordinance O-02-14, the owner is responsible for the sewer lateral from the point of origin on their property to property line, while the City is responsible for the sewer lateral extending down from the property line down to the sewer main, including all sections of sewer lateral line that may be under City sidewalks, curbs, streets, or alleyways. The City ensures that the policy is adequately communicated via a Sewer Lateral Maintenance Policy that is distributed to all property owners; incorporating the policy in the City’s Municipal Code; and by placing the policy on the City’s Website.  
5.9 Standardizations of Equipment and Sewer System Components
The City strives to standardize the equipment used in the sewer systems and the component parts to the sewer system. The criteria used for this standardization comes from the City’s Standard Drawings (See Appendix E). Standardization of the equipment and components serves to improve the operations, repair, and maintenance of the sewer system by eliminating dissimilar sewer system components and materials.
6.0 OVERFLOW EMERGENCY RESPONSE PLAN
The City developed standard Sanitary Sewer Overflow (SSO) procedures over a decade ago. This section documents the specific instructions, policies, and procedures for responding to SSO’s.  SSOs are classified in accordance with SWRCB Order No. 2006-0003. The categories of spills, the response and reporting requirements are detailed in the remainder of this section.

SSOs can be either: Category 1 - Greater than 1,000 gallons or and SSO that results in a discharge to a drainage channel and/or surface water; or to a storm drainpipe that was not fully captured and returned to the sanitary sewer system; Category 2 - Less than 1,000 gallons; or SSOs from private sewer systems and laterals.

Possible SSOs occur in one of three areas of the collection/treatment system as follows:

1. Collection System;

2. Lift Station; or

3. Treatment Plant

The response procedures for SSOs are determined by the classification and location of the SSO.  While the objectives of the response remain the same, the coordination and personnel chain of communication is slightly different. 

For spills on City property (i.e., at the Wastewater Reclamation Facility) on-site personnel report the spill to the Wastewater Reclamation Facility Manager who makes operational decisions regarding the containment, recovery, and clean-up. All documentation and reporting of the spill (SSO Report Form) is performed by the Wastewater Operation Manager or their designee.  

For spills in the public area (lift station or collection system), notifications are made to appropriate response personnel.  Upon arrival at the site, said personnel collection essential information regarding SSO location, potential cause(s), initial estimates of volume, containment requirements, etc.  Additional staff and equipment are dispatched based upon determinations made during the initial site evaluation. 

Every effort will be made to ensure that all reported SSOs are responded to within the first hour of notification of the SSO.
6.1 Purpose

The primary purpose of the Sanitary Sewer Overflow (SSO) Plan is to provide written guidelines that improve response time, provide clear guidance regarding containment, clean-up and reporting, and minimize the overall risks associated with SSOs. 
6.2 Goals and Objectives

The City recognizes its responsibility in protecting the public health and the environment. The goals of the SSO Plan underscore that responsibility. The goals of the SSO Response Plan are to:

· Ensure all reported SSOs are responded to immediately;

· Identify and allocate adequate resources needed in the response;

· Provide timely and adequate training, equipment and qualified staff to ensure effective response; and

· Ensure all SSOs are accurately reported and any SSO trends are identified and used to provide opportunities for continuous improvement.  
The objectives of the SSO Plan are to:  

· Reduce the occurrence and the magnitude of SSOs;

· Protect the collection system, wastewater treatment facilities, and all appurtenances;
· Protect public and private property;

· Protect water quality; and

· Protect Public Health, Safety, environment and property from SSOs.
· Prevent the discharge of sewage into surface waters.

· Contain the sewage discharged to the maximum extent possible. 

· Establish perimeters and control zones to control public access to SSO area.

· Prompt notification of spill information and potential impacts. 

6.3 Initial SSO Response Procedures

This section presents a strategy to mobilize labor, materials, tools and equipment to correct or repair any condition, which may cause or contribute to a SSO.  
6.3.1 Staff Instructions 

When a call of a possible SSO is received, all relevant information (e.g., time and date call was received, specific location, description of problem, etc.) is collected by the City.  This information is relayed to the appropriate staff member(s), who is (are) dispatched to the location to confirm and conduct an initial assessment of the problem.  Staff notifications are made by telephone or mobile radio. Staff members are dispatched immediately to the site of a SSO.  The SSO will be contained to the greatest extent possible utilizing available equipment and resources. The Wastewater Reclamation Facility Manager or their designee will receive information from the responding staff and decide if additional crews, materials, equipment and supplies are need. 

The primary responsibilities of each employee in the spill response team are summarized in the following table.  Additional details of the responsibilities are covered in the sections that follow.

	SANITARY SEWER OVERFLOW RESPONSE TEAM

	
	Responsibilities
	Contact Information

	First Responder
	· Provide initial evaluation of spill severity

· Call emergency services, as required

· Notify Spill Response Supervisor

· Stop spill and secure area as instructed by Spill Response Supervisor
	

	Wastewater Reclamation Facility Manager / Spill Response Supervisor 
	· Direct First Responder in initial actions to control spill and prevent public exposures to spill

· Evaluate spill and determine actions to control and cleanup  

· Notify Wastewater Operations Manager

· Mobilize City personnel/equipment to respond to spill

· Contact and direct outside services, as required, to respond to spill

· Complete Sanitary Sewer Overflow Report (field form) and initiate agency notifications

· Authorize City resources to respond to spill

· Communicate with Public Works and Regulatory Agencies. 
	Martin Guerrero 

(909) 370-5599 or Cell (909) 772-7895

	Public Works Director
	· Authorize City or contractors to respond to the spill

· Communicate with City Manager, Regulatory Agencies, and public information officer 
	Amer Jaker
(909) 370-6199

	Industrial Pretreatment 
	· Determine required sampling for spill and initiate investigation, as indicated, regarding potential sources of the cause of the SSO.
	G&G

(951) 789-5028

Cell (951) 858-1542


Table 6‑1 Spills Response Duties & Contacts
6.3.2 First Responder Duties and Responsibilities
The first City of Colton Employee who arrives at the site of a SSO has the primary responsibility of taking immediate actions to protect the health and safety of the public. Secondly, the first responder must ensure that proper notifications are made to the Wastewater Department to initiate a timely and effective response needed to minimize the risks associated with the SSO.  
If the first responder determines the SSO is not the responsibility of the City of Colton (e.g., private lateral spill) but an imminent danger exists to public health, property, or to the public waterways of the United States, then prudent emergency actions are warranted until the responsible party provides action to mitigate the SSO.  Upon arrival at a SSO, the first responder will:

· Determine the cause of the SSO, e.g. sewer line blockage, pipeline break, pump station mechanical or electrical failure;

· Identify and request, if necessary, additional personnel, materials and equipment to minimize the impact of the SSO; 

· Control public access to spill area; and

· If possible, take immediate steps to stop the overflow.
6.3.3 SSO Response Field Supervisor

The Spill Response Field Supervisor assumes primary management and coordination of all emergency activities and communicates with the Director.  The supervisor will be responsible for the official spill volume estimate; coordinating spill control and cleanup efforts; and notifying the proper state, county and local regulatory agencies.  The Spill Response Field Supervisor, or a designated City alternate, will fill out the Sanitary Sewer Overflow Report (See Appendix F).  

6.3.4 Wastewater Reclamation Facility Manager
The Wastewater Reclamation Facility Manager authorizes the expenditure of emergency response resources and communicates with the City’s Public Works. Additional outside resources, if needed, are contacted to assist with the SSO response.  Contact information for the additional outside resources can be found in Section 6.4.

6.3.5 Environmental Compliance Services
The Environmental Compliance Division (ECD) will determine the required sampling during spill evaluation and clean up. The ECD Coordinator will initiate an investigation as to the source and cause of the SSO.
The ECD will assist as directed regarding regulatory reporting of the SSO event.  
6.4 Initial Notification Procedures

The Sewer Overflow Response Procedure presents a strategy to mobilize labor, materials, tools and equipment to correct or repair any condition, which may cause or contribute to an unauthorized discharge. The City Employees or the public may detect an overflow, or report suspicious circumstances (unusual odors, flooding, etc.) which could indicate the possibility of an overflow.  The general flow of information is shown in Figure 6-10 at the end of Section 6. 
During normal business hours calls received by the police or fire departments will be routed or forwarded as shown in Figure 6-10 by the receptionist.  During after-business hours and weekends, calls received by the on call emergency answering service will be forwarded to the appropriate on call person.  Once police or fire department receives the initial report, the appropriate crews from the appropriate agencies will be dispatched. 
If the originating spill enters into areas outside the responding agency’s jurisdiction, the spill will continue to be contained and cleaned.  However, the affected agency will be notified of the spill to ensure proper notifications are completed.  
Upon arriving to respond to a spill, if it is found that the spill is outside of its jurisdiction, the responsible agency will be contacted to respond to the spill.  Until the responsible agency arrives, the initial responding agency will continue its efforts to contain and clean up the spill.

6.4.1 Emergency Call Out Lists
The City maintains a Confidential Contact List that includes key personnel within the City as well as vendors that may be called on to assist in the SSO Response.  The Table that follows (Include Table Reference Number) 
COLTON WATER RECLAMATION FACILITY

PERSONNEL ROSTER

2015
OPERATIONS-ON CALL LIST:

Name


Job Title

        City Cell Phone

Home Phone 

Ovidiu Bostan             Lead Operator                         772-7891

Anthony Abrams
Lead Operator 

559-3054
       
(909) 638-8330
Robert Eichner
WW Operator II

841-6686
      
(909) 677-6045
Martin Oliva

WW Operator I

772-9686
       
(909) 423-0363

Martin Guerrero
Wastewater Reclamation
772-7895
       
(909) 792-6368




Facility Manager
COMBINATION TRUCK OPERATORS-MAINTENANCE:
Name


Job Title

    City Cell Phone
  
Home Phone

Rick Shingleton
WW Equip. Mech. II

909-772-3480
        
909-336-4042
      
COLLECTIONS SYSTEM MAINTENANCE:

Name


Job Title


Cell Phone

  Home Phone

Victor Marquez
Collection Crew Manager
909-821-8940
Romell Eutsey

Collection Crew

909-835-9788

760-780-2254

Joel Schwartz

Collection Crew

909-295-2035

909-825-7850

John Coyazo

Collection Crew

909-518-7253



SPILLAGE REQUIRING LARGE PUMPER TRUCK:

K-Vac 


Environmental Service


        
(909) 476-2308
Houston and Harris
Contractor


721-1756
        
(909) 422-8990
CONTRACTED PRE-TREATMENT INSPECTION & LABORATORY SERVICES:

Gary Ethridge

G&G Environmental Compliance Inc.

(951) 858-1542
E.S. Babcock & Sons Laboratory Services
         
(951) 653-3351
[image: image48.jpg]



[image: image49.jpg]



Figure 6‑1 Sanitary Sewer Overflow Report

The City documents SSO information on a standard report form (Figure 6-1) that is initiated in the field and returned to the office for completion.  The form contains pertinent information that enables the electronic report (through CIWQS) to be easily completed and transmitted to the State. 
6.5 Assessment, Containment, Traffic Control and Clean-up
City employees are responsible for minimizing the affects of any SSO.  The following sections provide guidance’s for either the first responder or the SSO response supervisor in the event of a SSO.  
6.5.1 Preliminary Assessment of Damage to Private/Public Property

The first person at the scene gathers pertinent information and determines if the spill is a SSO.  Next, the SSO classification (i.e., Category 1, 2, or private lateral) is determined. Regardless of the classification, all SSOs are treated in the same manner. The first priority is to contain and cleaned up the area before the SSO reaches a storm drain.  Once containment and clean up is under control, documentation and reporting become priorities. In addition to accurate reports, photographs are taken to document the spill and the procedures used for containment and cleanup.  Once a Sanitary Sewer Overflow (SSO) Report form is received, the field notes can be transcribed to the SSO Report form. 
6.5.2 Containment
After the initial assessment, all reasonable efforts will be made to contain the SSO (e.g., install plugs, sandbags, sand/rock, etc.) 
6.5.3 Traffic and Crowd Control

The traffic and crowd control used for the SSO situations can be summarized as follows:

Spills (less than 1,000 gallons)

A. Setup traffic cones to direct traffic from spill area.

B. Use staff personnel to control traffic and pedestrians.

Spills (1,000 to 10,000 gallons)

A. Contact Mutual Aid Contract cities as needed.

B. Perform lane closures as needed.

C. Close any affected entrances or exits from all public and private facilities.

D. Place proper signage for any lane closures including contaminated area signs.

E. Use caution tape and barricades to protect pedestrians from contaminated area.

Spills (> 10,000 gallons)

A. Assess spill situation.

B. Contact Mutual Aid contract cities as needed. 

C. Inform local police and sheriff’s department of any law enforcement needed road closures and traffic control.

D. Delegate the responsibilities to Mutual Aid team members to inform public of hazards also use signage to inform public of potential hazards to public health and safety.

E. Block public access to hazard using barricades, cones and caution tape.
6.5.4 Initial Estimates of Flow Volume
Initial estimates of flow volumes are through on-site observations using best professional judgment and guidelines established by recognized engineering firms and other municipal agencies.  The Best Practices Guidelines shown on the following pages are used in making initial estimates of overflow volumes.  Final numbers are confirmed during cleanup and recovery efforts based upon volumes returned to the sewer and estimates of unrecovered volumes.

[image: image7.jpg]Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and
Response Plan

Sample Templates for SSO Volume Estimation

TABLE A"
'ESTIMATED SSO 1 QW OLIT OF MH WITH COVER IN PLACE.
24 couer 38" cover
T S T o seee]
T Lo o v Ny i oy
T [oen T
S loze) 2 bl

Dislaimer.
T sandary sewer overfow table was develope by Ed Euyen, Civil Engineer. P No. 33055,
‘Cakforia for County Santation Distric 1. This tabl s provided a5 an sxampe. Other Agencies
may want o develop heir own estimating tabies




[image: image8.jpg]Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and
Response Plan

‘The formula used to develop Table A measures the maximum height of the water
coming out of the maintenance hole above the rim. The formuia was taken from
hydraulics and its application by A H. Gibson (Constable & Co. Limited).

Example Overflow Estimation:
“The maintenance hole cover is unseated and slightl elevated on a 24" casting

‘The maximum height of the discharge above the rim is 5 % inches. According to
‘Table A, these conditions would yield an SSO of 185 galions per minute.

Height to be measured

‘This sanitary sewer overflow drawing was developed by Debbie Myers, Principal
Engineering Technician, for Ed Euyen, Civil Engineer, P.E. No. 33955, Califomia,
of County Sanitation District 1




[image: image9.jpg]Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and
Response Plan

TABLE 'B'
ESTIMATED S50 F1 QW QUIT F MJH WITH COVER BEMOVED.
24" ERAME 36" ERAME
Jrsgn o s 50 uom ae maner g s s 50 rLom e m e
rvama |0 e ity i i
P R
i o b -
: Fa
it 250 |7
i 3 |see
Disciaimer:

‘This sanitary sewer overflow table was developed by Ed Euyen, Civil Engineer,
P.E_No. 33955, Calfomia, for County Sanitation District 1. This table is provided
as an example. Ofher Agencies may want to evelop their own estimating
tables.




[image: image10.jpg]Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and
Response Plan

‘The formula used to develop Table B for estimating SSO's out of maintenance
holes without covers is based on discharge over curved weir - bell mouth
spillways for 2" to 12" diameter pipes. The formula was taken from hydraulics
and s appiication by A H. Gibson (Constable & Co. Limited).

Example Overflow Estimation:

“The maintenance hole cover is off and the flow coming out of a 36" frame

‘maintenance hole at one inch (1°) height will be approximately 660 gallons per
minute.

FLOW OUT OF M/H WITH COVER REMOVED (TABLE "B")
Height to be measured

‘This sanitary sewer overflow drawing was developed by Debbie Myers, Principal
Engineering Technician, for Ed Euyen, Civil Engineer, P.E. No. 33955, Califomia,
of County Sanitation District 1




[image: image11.jpg]Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and
Response Plan

ESTIMATED SS0 FI OW OUT OF MM PICK HOLE.

o | S0 e
e i o riow
[y [t R
e | gt 20 | wmcnenn

Note: This chart’s based on a 7/8 inch diameter pick hole:

Disclaimer: This sanitary sewer overflow table was developed by Ed Euyen, Civil
Engineer, P.E. No. 33955, Calfornia, for County Sanitation Distrct 1. This table
is provided as an example. Other Agencies may want to develop their own
estimating tables.




[image: image12.jpg]Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and
Response Plan

‘The formula used to develop Table C is Q=CcVA, where Q is equal o the
‘quantity of the flow in gallons per minute, Cc is equal to the coefficient of
contraction (53, V is equal to the velocily of the overflow, and A is equal to the.
area of the pick hole.2 Ifall nits are in feet, the quanty will be calculated in
cubic feet per second, which when multplied by 443.8 wil give the answer in
gallons per minute. (One cubic foot per second is equal to 448 8 gallons per
‘minute, hence this conversion method).

Example Overflow Estimation:

‘The maintenance hole cover is in place and the height of water coming out of the
pick hole seven-eighths of an inch in diameter (7/8")is 3 inches (3). This wil
produce an SSO flow of approximately 47 gallons per minute

FLOW OUT OF VENT OR PICK HOLE (TABLE

Height to be measured

‘This sanitary sewer overflow drawing was developed by Debbie Myers, Principal
Engineering Technician, for Ed Euyen, Civil Engineer, P.E. No. 33955, Califoria,
of County Sanitation District 1

*Velocsy fo thepposes of i ol s calclated by sing the formula = squared /26, wherehis
equal o e beight of e avein, s equl 1 eloiy, ad G s cqul o h acelrsion o g2y




[image: image13.jpg]Response Plan

Collection System Collaborative Benchmarking Group
Best Practices for Sanitary Sewer Overflow (SSO) Prevention and

:
2
=
g
]
Z
o
F
g

[ —"
Seiouuely omss.
i1 amas Buteuns3 103 35005 2RIy





Figure 6‑2 Estimating SSO Volume

6.5.5 Additional Measures for Prolonged SSO Conditions

· Set up a portable by-pass pump operation around problem/obstruction.  Contractors may be utilized in the event of a prolonged SSO. 

· Implement continuous or periodic monitoring of the by-pass pumping operation as necessary.
6.5.6 Clean-up

All SSO sites are to be thoroughly cleaned after an SSO (i.e., no readily identifiable residue is to remain).  SSO Clean up procedures include:
· Where practical the area is thoroughly flushed and cleaned of any sewage using high-pressure water hose or Combination truck.  Solids and debris are flushed, picked-up and hauled away.  All flush water will be contained and collected for proper disposal. 

· The SSO site is secured to prevent contact by members of the public until the site has been thoroughly cleaned.  Posting of signs, if required, concerning public health and safety will be undertaken pursuant to Section 6.18.1. 
· The SSO site should be disinfected and deodorized using liquid bleach (sodium hypochlorite), etc. Caution needs to be used to ensure that any disinfection chemicals used, do not contribute to or cause violations of other NPDES Permit requirements related to chlorine levels in waterways.  

· Ensure proper contact time for proper disinfection.

· Where sewage has resulted in ponding, pump dry and remove all residues.

· If sewage has discharged into a body of water that may contain fish or other aquatic life, do not disinfect, contact appropriate agency for further instructions.
6.5.7 Monitoring

6.5.7.1 Surface Water Spill 
· Water quality samples must be taken in the event sewage enters surface water.  

· Samples must be taken upstream and downstream of any surface water.  

· The sample location and time will need to be logged on the chain of custody form. 
· A map of the sample location(s) should be made so that follow-up testing is performed at the same location(s).  

· The employee taking the samples will start at point of entry.  When taking the sample, submerge the bottle below the surface of the water with the cap on.  Once the bottle is under the surface, remove the cap and fill the bottle.  Gloves will be worn while sampling to avoid infecting any open wounds.

· Spill should be analyzed, at a minimum for:

· pH; E/C; Ammonia Nitrogen;

· Biochemical Oxygen Demand (BOD);

· Dissolved Oxygen (DO);

· Total Fecal Coliform;

· Total Suspended Solids (TSS); and 

· Any other constituents as directed by the RWQCB or by the City’s Environmental Control Section.

6.5.7.2 Ground (Non-Surface Water) SSO
SSOs to the ground that do not reach surface waters are monitored in accordance with any requirements stipulated by the RWQCB.
6.6 Private Property SSOs

The City will respond to all SSOs within their service area.  If determined that a SSO originated from a sewer lateral or septic system on private property, the City will assist in the control and containment to ensure that the wastewater does not enter into storm drains, spillways, etc.  The property owner will be informed of the blockage; the City’s Private Lateral Sewer Policy (See Appendix F) and will be responsible to remove the blockage.  If the SSO was a result of the sewer trunkline, the response crew will correct the problem. In each case, the City will report the spill in accordance with Section 6.8 of this Plan.
6.7 SSO Reporting

Forward SSO reports to the RWQCB and other authorities as summarized in Section 6.15, Sewer Overflow and Discharge Reporting.  Each category of SSO (e.g., Category 1 and 2 and the private lateral sewage discharge) having different reporting timeframes.  Said timeframes are included in Section 6.14.  Complete reporting requirements (General Order No. 2006-0003-DWQ) and recent revisions (Order WQ-2008-0002-EXEC) are included in Appendix A.  

Electronic reporting of all Category 1 and Category 2 SSOs is required.  Electronic reporting of private lateral sewer spill reporting is voluntary but encouraged.  

Please note that voluntary reporting of private lateral sewer overflows during a calendar month does not eliminate the requirement to submit a “No-spill Certification” if a Category 1 or Category 2 SSO did not occur during that month.  All SSO reports are considered drafts until the Legally Responsible Official (LRO) verifies the accuracy of information prior to certification.  In some cases, draft reports are certified as drafts (in cases where all required information has not been received or verified). Detailed reporting requirements including timeframes for reporting are contained in the Monitoring and Reporting Program (MRP) section of the WDR. The WDR requires SSO reports to be retained for a minimum period of five years from the date of the incident.  Reports older than five years may be archived in accordance with approved City record management practices.
6.8 Regulatory Agency Notification Plan

The Regulatory Agency notification plan establishes procedures, which the City of Colton will follow to provide formal notice to the RWQCB, Office of Emergency Services (OES), Department of Environmental Health Division of San Bernardino County, and other agencies as necessary in the event of a SSO.  Notifications to the RWQCB are verbal, electronic, or by fax (when the electronic data-base is not functioning) and shall be performed in accordance with specific requirements contained in Attachment A of the SSO.  Verbal notifications to other regulatory agencies shall be at the same time the Regional Board is notified. 

Notifications to the Regional Board under the Monitoring and Reporting criteria listed in the General Order for Sanitary Sewer Systems do not preclude the City from reporting SSOs to other regulatory agencies pursuant to California state law. SSO shall also be reported to OES, in accordance with California Water Code Section 13271 and to County Health officials in accordance with California Health and Safety Code Section 5410 et seq. The SSO database will automatically generate an e-mail notification to the appropriate County Health Officer and/or environmental Health Department and the appropriate Regional Water Board with customized information about the SSO upon initial reporting of the SSO and final certification for all Category 1 SSOs. Written notifications to other regulatory agencies, when required, shall be made within five (5) business days of the initial notification. 
6.8.1 Initial Notification

For any SSO that results in a discharge to a drainage channel or surface water: The City of Colton must a.) notify the State Office of Emergency Services, b.) the local health officer or directors of environmental health services, and c.) the Regional Water Quality Control Board as soon as possible, but in no case later than two (2) hours after becoming aware of the discharge.  

The City must also certify to the Regional Board, as soon as possible, but no later than twenty-four (24) hours after becoming aware of a discharge, that a.) the State Office of Emergency Services and b.) the local health officer or directors of the applicable environmental health agency have been notified of the discharge. The Regulatory Agencies will be contacted by the Supervisor/Manager in charge.

Category 1 SSOs require the City to file an initial report to the Online SSO tracking system as soon as possible but in no case later than three (3) business days after the city is aware of the SSO. A final certified report must be completed within fifteen (15) calendar days of the conclusion of the SSO response and remediation.

Category 2 SSOs must be reported to the online Database tracking system within 30 days after the end of the calendar month in which the SSO occurs. (e.g., all SSOs occurring in the month of January must be entered into the database no later than March 1st.)

If no SSOs occur during a calendar month, the City must file an electronic report through the Online SSO Tracking certifying that no SSOs occurred during the designated month.

If the SSO Online database is not available, the City must fax all required information to the Regional Board office in accordance with the time schedules listed above.
It is important to gather essential information during each SSO.  To be able to file adequate electronic reports, certain mandatory information must be collected.  The following list represents, at a minimum, the information required before finalizing and certifying an SSO Report. 

Category 2 SSOs:

A. Location of SSO (GPS Coordinates);

B. Applicable Regional Water Board, i.e. identify the region in which the SSO occurred;

C. County where SSO occurred;

D. Whether or not the SSO entered a drainage channel and/or surface water;

E. Whether or not the SSO was discharged to a storm drain pipe that was not fully captured and returned to the sanitary sewer system;

F. Estimated SSO volume in gallons;

G. SSO source (manhole, cleanout, etc.);

H. SSO cause (mainline blockage, grease, roots, etc.)

I. Time of SSO notification or discovery;

J. Estimated operator arrival time;

K. SSO destination;

L. Estimated SSO end time; and

M. SSO Certification – upon SSO Certification, the SSO Database will issue a Final SSO ID Number.

Private Lateral Sewage Discharges:

A. All information listed above (if applicable and known), plus:

B. Identification of sewage discharge as a “private lateral sewage discharge”; and

C. Responsible party contact information (if known).

Category 1 SSOs:

A. All information listed for Category 2 SSOs plus:

B. Estimated SSO volume that reached surface water, drainage channel, or not recovered from the storm drain;

C. Estimated SSO amount recovered;

D. Response and corrective action(s) taken;

E. If samples were taken, identify which regulatory agencies received sample results (if applicable).  If no samples were taken, NA must be selected;

F. Parameters that samples were analyzed for (if applicable);

G. Identification of whether health warnings were posted;

H. Beach impacts (if applicable).  If no beach is impacted, NA must be selected;

I. Whether or not there is an ongoing investigation;

J. Steps taken or planned to reduce, eliminate, and prevent reoccurrence of the overflow and a schedule of major milestones for those steps;

K. OES control Number (if applicable);

L. Date OES was called (if applicable);

M. Time OES was called (if applicable);

N. Identification of whether County Health Officers were called;

O. Date County Health Officer was called (if applicable); and

P. Time County Health Officer was called (if applicable).

6.8.2 Secondary Notification

After those parties on the mandatory notification list have been contacted, the City of Colton will contact the other regulatory agencies as necessary, as well as other impacted parties if there has been an overflow. 
6.8.3 Electronic Reporting Procedures

Sanitary Sewer Overflows (SSOs) are reported electronically to the State Water Resources Control Board. Spill reports must be entered into the California Integrated Water Quality System (CIWQS), which can be found at https://ciwqs.waterboards.ca.gov/. (See Screen Print below)

[image: image14.jpg](O CALIFORNIA ENVIRONMENTAL PROTECTION AGENCY

6 GOV STATE WATER RESOURCES CONTROL BOARD





	Top of Form

California Integrated Water Quality System (CIWQS) 
 

User ID:
[image: image15.wmf]


Password: 

[image: image16.wmf]


[image: image17.wmf]Login



 HTMLCONTROL Forms.HTML:Hidden.1 [image: image18.wmf]

true



 HTMLCONTROL Forms.HTML:Hidden.1 [image: image19.wmf]


Forget your password? Reset your password here.
Bottom of Form

Contact Us
 


Figure 6‑3 CIWQS Log-in Screen Shot
Sign in using the login name and password that has been set up and assigned to identified wastewater plant management and staff. Once signed in, the next screen will look like the screen print shown in Figure 6-4.

	Menu | Help | Log out 

	Navigate to: [image: image20.wmf]

SSO



	Regional Water Board:
	Region 8 - Santa Ana

	Agency:
	Colton City

	Sanitary Sewer System:
	Colton Water Reclamation Facility CS


	

	· Collection System Questionnaire     ?  
Pertinent information regarding your collection system. 

· Sewer System Management Plan (SSMP) Certification     ?  
Certify SSMP completion/compliance 

· Reporting New SSO     ?  
Report new SSO. 

· Modifying Existing SSO     ?  
View/Modify existing SSO Report. 

· View No Spill Certification     ?  
View no spill certification. 


Figure 6‑4 SSO Electronic Reporting CIWQS Menu Screen
From this menu, select “Modify Existing SSO”.  The next screen will prompt the user to create either a new SSO report or Search (bottom of page) for an existing SSO Report.  Select “Search” and a report similar to the one shown in Table 6-2 is generated.  The CIWQS System will generate a listing of all reported SSO’s with the SSO Event ID. The Event ID is linked to detailed information from each event. 

[image: image50.emf]Region

Responsible 

Agency

Collection 

System 

Number of 

SSOs

Total SSO 

Volume(gal) 

Total Vol Recover (gal) 

Total Vol Reach Surface Water 

Percent Recover 

Percent Reach Surface Water 

Miles Pressure Sewer 

Miles Gravity Sewer 

Miles of Laterals 

Total Number of SSO 

locations per 100 miles of Sewer 

Tot Vol of SSOs Reach Surface 

Water per 100 miles of Sewer 

WDID 

8 Colton City 

Colton Water 

Reclamation 

Facility CS 

1 25 25 0 100 0 4 110 0 0.8 0 8SSO10636

1 25 25 0 4 110 0


Table 6‑2 CIWQS Spill Report Summary
6.8.4 Spill Report Debriefing
After the sewer spill has been mitigated and no more than one week after the incident, a spill-debriefing meeting should be held to discuss any problems encountered during each phase of the spill response procedure.  All personnel involved with the incident are to attend and ensure the spill debriefing meeting presents an opportunity to correct any noted deficiencies and to better prepare for and respond to future SSOs.
6.9 Collection System Mapping

The City of Colton maintains maps of the collection systems and the storm drains as either a sewer atlas, updated on a regular basis, or electronically in the form of Geographic Information System (GIS).  Utility maps are available via the City intranet.  Figure 6-4, on the next page, is a screen print that illustrates the types of information available electronically on the City’s Intranet.

Sewer Atlas maps are located at the RWRF Operations Center and a copy is placed in each sewer collection vehicle.  The contracted line cleaning company has access to all sewer maps as well.  

[image: image51.emf][image: image52.emf][image: image53.jpg]


[image: image54.jpg]


[image: image21.jpg][




[image: image22.png]Welcome to the Colton Intranet












COLTON INTRANET | CITY PROGRAMS 



· [image: image55.jpg]


Performance Impact

· SPL / Synergen

· As-Built Retriever 

· Geo Viewer
· Property Viewer
· Utility Viewer 
›CITY PROGRAMS 

Figure 6‑5 City of Colton Intranet Utilities
City employees can access the City’s Intranet to view a variety of on line plans and maps that assist the City in determining locations, sizes, and routing of many of the City utilities.  For example, by clicking on the Utility Viewer, the location of sewer lines, manholes, street views, etc., can be retrieved and printed for use in the field.
Examples of the types of maps and information that can be reviewed electronically before responding to a sewer call are shown on the next several pages.

[image: image28.jpg]S
Printed: 3/3/2009 12:14:47 PM

City of Colton Boundary & Sewer Lines
Sanitary Sewer Management Plan (SSMP)

I:I City Boundary

,\/ Sewerlines

/\/ Freeways
Streets

Santa Ana
River

Surrounding
City Streets

This map is a public resource of general information. This map was produced by the City of Colton
Geographic Information Systems Department. The base data is acquired from San Bernardino County
GIMS Department. The City of Colton assumes no warranty or legal responsibility for the information

on this map. The data and information are subject to change without notice.




Figure 6‑6 City of Colton Boundary Map

[image: image29.jpg]RWRF Incoming Lines

Features

City Boundary
Manholes
Sewerlines
Freeways
Streets

Santa Ana
River

Parcels

Surrounding
City Streets

This map is a public resource of general information. This map was produced by the City of Colton
Geographic Information Systems Department. The base data is acquired from San Bernardino County
GIMS Department. The City of Colton assumes no warranty or legal responsibility for the information

on this map. The data and information are subject to change without notice.

S
Printed: 3/3/2009 12:31:03 PM





Figure 6‑7 Colton WRF and Incoming Sewer Line Map

[image: image30.jpg]Residential Manholes & Sewer Lines

|_Il City Boundary
& Manholes
/\/ Sewerlines
! Streets
e (7S srnene ‘ - - Addresses

E Surrounding
City Streets

N X 2 @ ﬂ
.:‘.' H\\J‘g .s ‘l.i,
- B

l\x

.

e

This map is a public resource of general information. This map was produced by the City of Colton
Geographic Information Systems Department. The base data is acquired from San Bernardino County
GIMS Department. The City of Colton assumes no warranty or legal responsibility for the information

on this map. The data and information are subject to change without notice.

S
Printed: 3/3/2009 1:11:20 PM





Figure 6‑8 Manhole and Sewer Line Map (Partial)

6.10 Training

The Environmental Conveyance staff will participate in training sessions scheduled with appropriate staff in one of the three different types of training which would demonstrate the strengths/weaknesses of the SSO.  The three different types of training exercises include:

· Orientation Exercise:  Exercise consisting of brief lecture/overview of the requirements/ past experiences.  It will serve as a session to instruct employees on plan and required documentation. 

· Tabletop Exercise:  SSO is simulated, without actual deployment of equipment or resources.  Participants play through discussion and the use of a facilitator.  Exercise effectiveness is determined by the feedback from participants and impact on revisions to plans, procedures and systems. 

· Functional Full Scale Exercise:  A spill event is simulated during the exercise.  Controllers monitor the play, and observers record the player’s actions.  The exercise will provide opportunity to evaluate the plan’s objectives.  It will also test equipment, response time, training, resource, and man-power capabilities.  

Records of training and event participation will be recorded and maintained.  

6.11 Public Advisory Procedure

All media inquiries will be directed to the City of Colton, Public Information Officer/Department Head.
6.11.1 Temporary Signage

In public accessed areas, signage and barriers must be in place for the duration of the cleanup and disinfection process.   Signs warning the public of a sewage release should be posted, in English and Spanish in the affected area.  Signs should include, at a minimum, the wording of “raw sewage” (See examples on the following page).  Warning signs should remain posted until the Department of Environmental Health Division of San Bernardino County or RWQCB staff authorizes their removal, or until receiving sample results indicate background levels (levels determined by upstream samples) have been attained.

[image: image31.png]Brgh

WARNING!
RAVWSEWAGE SFILL.

AREACLOSED
KEEF OUT

BINIAGIEBITAL COMPLLAICE DIVZION
CZEev





Figure 6‑9 Sewage Spill Sign - English
[image: image32.png]AREA CERRADO
FROHIBIDO ELFASO

DIIZION DB LACUMPLIIBITO AMEIBITAL
Do) 0123





Figure 6‑10 Sewage Spill Sign - Spanish

6.12 SSO Plan Maintenance

6.12.1 Submittal and Availability of the SSO Plan
The SSO Plan is not submitted to the State or Regional Board.  The SSO Plan must however, be available for their review during routine inspections.  As such, the SSO Plan will be available at the City of Colton Wastewater Treatment Plant Administration Building in both hard copy and electronic versions.  

6.12.2 Review and Update of SSO Plan
The SSO Plan is a dynamic document and will be reviewed and revise to reflect current policies and procedures as needed.  The SSO Plan will be reviewed each year in July.  The annual review of the plan will also insure all provisions of the plan are being met and implemented.  Any SSO plan deficiencies and updates will be identified and corrected. Any proposed changes to the SSO Plan will be adequately communicated and reviewed. Changes become final when approved by the Public Works Director. 
6.13 Tracking SSOs

Sanitary Sewer Overflows (SSOs) are tracked using the same system that is used for electronic reporting to the State Water Resources Control Board. Namely, the CIWQS system, which can be found on the State web-site:

https://ciwqs.waterboards.ca.gov/. 

Sign in using the login name and password that has been set up and assigned to identified wastewater plant management and staff.
The Summary Report is an excellent tool for looking at spill history at a glance that shows how many spills occurred during certain time-frames; the volume of each spill; the location; and other important information that helps the city identify causes and history patterns that may serve as indictors for SSMP improvement opportunities. The following Report can be generated by going to the State Water Resources Control Board SSO Public Report web page at: 
https://ciwqs.waterboards.ca.gov/ciwqs/readOnly/PublicReportSSOServlet?reportAction=criteria&reportId=sso_overview. 
Select SSO Report and then fill out the City and or Zip Code area you are searching and the time-frame(s) of interest.
[image: image56.jpg]ENVIRONMENTAL
COMPLIANCE, INC.

pr =




Table 6‑3 SSO Summary Report - CIWQS
Most tables on the CIWQS website can be saved as Excel Spreadsheets for further data analysis if necessary.  The City of Colton will use the Reports for identifying deficiencies in the current program and for evaluating the best methods for improving the effectiveness of the SSMP.
Additionally, a “No-Spill Certification” Report can be generated that indicates all months where no SSO occurred. A sample copy of the No Spill Report Certification is shown in Table 6-4..

	Top of Form

No Spill Certification:
I certify under penalty of law that no spills occurred for the month specified below. Based on my inquiry of the person or persons who manage the system, or those persons directly responsible for gathering the information, the information submitted is, to the best of my knowledge and belief, true, accurate, and complete. I am aware that there are significant penalties for submitting false information, including the possibility of a fine or imprisonment, for knowing violations. Clicking the "Certify" button below indicates my certification of this report and my understanding of the above conditions. 
Month/Year Without Spills:*
[image: image33.wmf]

- Select Month -



 HTMLCONTROL Forms.HTML:Select.1 [image: image34.wmf]

- Select Year -




	Confirmation Number

No Spill Certificate for the Month of

Entered Date/Time

Certified By

482685

Jan-07

2007-2-20.11.17. 53. 0

Eric Fraser

803283

Oct-08

2008-11-12.10.28. 18. 0

Mike Itnyre

801718

Sep-08

2008-10-29.14.7. 26. 0

Mike Itnyre

793384

Jun-08

2008-8-26.10.3. 38. 0

Eric Fraser

793385

Jul-08

2008-8-26.10.4. 24. 0

Eric Fraser

762179

Jul-07

2008-6-12.8.18. 59. 0

Eric Fraser

762180

Aug-07

2008-6-12.8.19. 41. 0

Eric Fraser

762177

Apr-07

2008-6-12.8.17. 56. 0

Eric Fraser

Previously Submitted Months with "No Spill Certification" 


Table 6‑4 CIWQS No-Spill Summary Report

[image: image35.emf]FLOW CHART

SANITARY SEWER OVERFLOW RESPONSE PLAN

SPILL OCCURS/REPORTED DURING

REGULAR WORK HOURS SPILL OCCURS/REPORTED

DURING NIGHTS AND WEEKENDS

Report of Spill

Received by Water -

Wastewater

Department

Public

Other

Source

Wastewater

Treatment Plant

Manager or Lead

Operator Directs the

Response Team to

Investigate the Spill

Call

SSO Report Form

Response Team Assess and

Categorizes SSO

(Responds in Accordance with

Established Written Procedures)

Yes

Private Lateral

Spill?

No

Determine Cause & Mitigate

(Contain Spill, Secure Area with

Barriers & Signs,

Prepare Incident/Spill Report

Clean-Up & Disinfect Area)

Communicates Spill Information

Category 1

Spill?

Category 2 Spill

Initial Notification

to OES, SB County

Health, and RWQCB

within 2 hours of spill

awareness

Certification to

RWQCB

as soon as possible (but no

later than 24-hours)

Did Spill

Reach a Drainage

Channel or Surface

Water?

Yes

Within 30-Days

Yes

Certified e-Report

Submitted

Provide Information Regarding

Responsibility for Maintaining Lateral

and Assist as Needed to Minimize

Public Health Risks

Initial Report within 3-Business Days

Final Certified Report within 15-Days

Voluntary

SSO

Resolved?

No

Yes

End of Action - File

Report(s)

Notify

Manager

Elevate Response to City Government

Level Necessary to Protect Health,

Welfare, & Resources as Directed

Report of Spill

Received by City PD

Dispatcher

On-Call

Wastewater Staff

Notified

Evaluates

Information Received

& Responds to

the Site

No

Notify Manager,

File Report, End

Response

Sanitary

Spill?

Data Input into

CIWQS System

No

Yes

No

Yes

Collect Water

Samples

as Determined by

RWQCB


Figure 6‑11 SSO Response Flow Chart

7.0 FATS, OILS, AND GREASE CONTROL PROGRAM
The City of Colton has an approved Pretreatment Program (Program) and conducts inspections at a wide range of commercial and industrial facilities including food service operations.  The legal authority for the Program is Ordinance No. O-02-15. FOG Control Program language was included in the revised legal authority language prepared in September 2008. The City’s enforcement Response Plan (ERP) has also been revised to include BMP language and enforcement steps needed for the FOG Control Program.  The following sections in this chapter describe the FOG Control Program.  
7.1 Background
The discharge of fats, oils, and grease (FOG) from animal and vegetable sources can create sewer line stoppages that result in sanitary sewer overflows (SSOs).  Two main sources of FOG discharges are from the restaurant industry and similar facilities (e.g. cafeterias, penal institutions, schools, colleges, and universities with food services, and commercial kitchens) and residential users.  The FOG discharges may be a result of poor housekeeping practices at restaurants and from poorly informed decisions by residential users.  The result is the same: SSOs. 

The discharge of hot or warm FOG materials to the sewer causes the quickest stoppage problems due to the receiving environment.  The sewer line temperatures typically range from 70 –80 degrees Fahrenheit.  Dishwashing machine temperatures are often as high as 160( F. At this temperature and when combined with detergent, FOG is emulsified. Without proper detention time in a grease interceptor, the FOG simply passes through to the sewer where it combines with cooler waters, solidifies, and adheres to the interior surfaces of a sewer line. The adhesion sites become future sites for additional adhesions much like making a candle.  A source discharge of FOG will create a blockage pattern in the sewer line characteristic of the material discharged and the frequency of discharge.  The blockage tends to increase in size downstream of the user’s lateral connection to the sewer.

Grease interceptors are gravity separation devices to separate FOGs and solids from the wastewater discharge by allowing heavy FOG to be collected through settling and floatable FOG through plumbing configurations that retain fluids in the upper layers of the interceptor (See Figure 7-1).  The use of biological or chemical agents in grease interceptors to liquefy FOGs prior to discharge is problematic.  Bacteria and enzymes act by reducing the long chain fatty acids into smaller chain molecules.  
A bacteriological system, even under ideal environmental conditions takes 24 – 72 hours to convert the FOGs to carbon dioxide and water.  Restaurant grease interceptors typically have low pH (below pH 6) and often lack adequate oxygen to support a good environment for bacteria.  Therefore, the City’s Municipal Code prohibits the use of such additives as a means of maintaining the interceptor.  

Gravity separation interceptors are sized based upon flow rates through the unit and a two-hour minimum detention time is required during the plan review process.  The result of bacterial or enzymatic product usage is a liquefaction or emulsification of the FOGs in the interceptor.  When liquefied FOG is discharged to the sewer where any further degradation of the FOG by the bacteria or enzyme is prevented due to the dilution of the material and other interferences in the receiving sewage.  The liquefied FOGs begin to adhere to sewer line interior walls, deplete the oxygen content of the wastewater due to the natural degradation microbes present in wastewater, and create odor problems due to the depleted oxygen content. These products are also prohibited by the City’s Municipal Code.
[image: image57.emf]
Figure 7‑1 Standard Interceptor Drawing
The City of Colton’s (City) FOG Control Program regulates the discharge of FOGs to the sewer system and provides best management practices information to the restaurant community and homeowners about managing FOG. 

7.2 FOG Program Elements

The City utilizes the following control techniques to minimize the discharge of FOG to the City’s sewer collection system (collection system).  

1. Site inspections
2. Database Tracking System
3. Public education and outreach

4. Collection system cleaning and assessments

5. Collection system and sewer lateral closed circuit television (CCTV) inspection

6. Timely resolution of non-compliance through site inspections, application of BMPS, the City’s Municipal code 13.08; and the approved ERP. 

7. Grease interceptor retro fits

8. Training

7.3 Site Inspections

[image: image58.bmp][image: image59.jpg]



Inspections of restaurants and similar sites enable the City to determine which sites may be problematic to the area’s collection system.   The City’s Environmental Compliance Department (ECD) is responsible for inspecting all restaurants and similar facilities within the City’s service area minimally once per year, with many being inspected two to four times per year.  The increase in inspection frequency is determined by a variety of factors including: the history of the site; the type of restaurant; presence of a grease interceptor; complaint history; history of sewer-line stoppages; or SSO history.  The photos above show a completely plugged grease interceptor chamber and the resulting wastewater overflow.  Failure to maintain grease interceptors results in this level of grease buildup and subsequent wastewater overflow. The site inspections are used to ensure proper maintenance and the results of said inspection are maintained in a computer relational database in the ECD that has the ability to provide the inspector with an inspection and enforcement history for the site. The screen print in Figure 7-3 indicate the main menu screen for the FOG Control Program database tracking and enforcement system used by the City.

[image: image36.jpg]= LinkoCTS Events and Scheduling - CTS - Compliance Tracking Software
I LnkoCTs  Reporting  Modules  Launch  Help

SelectBy: O Industry @ Group GrouplFilter Complete All Close

Industry Group:[FOG User [-] category{AlEvent Cetegories - Update Due | Auto Scheduler
Group: [AlTEverts -

Due Date:[any 2 Delete Calendar

Config

i iy 1SV N0, Industy lame Site Address 1 EventType  DueDate Completed Viola Late Complet Event Comments

Add New Date e
Detalls FLG Bugers TE0W ValleyBivd ANNUAL | 12312015 | B352015 A s Tacly epectan: PASS
Details_[F0G052 BurgerKing [CLOSED] Z02E Valey ANNUAL | 12312015 | 03252015 {An arual acily nspection: Cosed  now
Detalls_|FOG055 Fey's Ao Service 523 East Vally Boulevard ANNUAL | 12312015 | 03252015 (An e feciiy mspecion: Dy facity
Detalls_|FOG00 Ratos Ties FTWesl Vally Bodevard | ANNUAL | 12312015 | 03252015 {An el acity nspecton: Dy faciity
Details_|FOG057 Lo CarclaFlesta F10W Valey ANNUAL | 12312015 | 03252015 {An el acily nspection: PASS: BV poster
Dotails_[FO503% Fizza Fiut 20T E Washingion St ANNUAL | 12312015 | 03252015 {An el acily nspection: PASS; nferceptor,
Dotails_[FOG087 (Gbezzo's Auto Certer 32T N Mot VemonAve | ANNUAL | 12312015 | 03252015 i vl acily mspecton: PSS
Details_[FO5058 Lengs Fica Taco AT Valey ANNUAL | 03302015 | 03252015 PASS: Bip posterdefvered
Detalls_|FOG05 Colon Fladialor 5 East Vally Boulevard ANNUAL | 12312015 | 03252015 (AuloS checled by Annual Inspection
Dotails_[FOG080 WieDoralds ZBW Valey ANNUAL | 11272015 | 03252015 FASS
Details_[F05032 FapaJobrs TETEE Washingion St ANNUAL | 03302015 | 03242075 RS toke out  delvery
Details_[F06135 [Diesel Infection Servies. B30 AsHiey Wy ANNUAL | 12312015 | 03242075 {An el acity nspection: PASS; lafer on
Detals [FOGTZT (Gne Stop Ao Care [T703E Washingon SuleE | ANNUAL | 12312015 | 03262015 ‘Ar el acily inspecton: PASS
Details_[F06-089 The Tie Shon 22295 LaCadena D ANNUAL | 12312015 | 03242075 Pivate resdence?
Details_|FOG-020 o Verenda Mai (CLOSED] 295 N M Veman Ave ANNUAL | 12312015 | 03242075 Facity closed
Details_[FOGTT Carwash 701 E Washingion St ANNUAL | 12292015 | 03242075 PASS; ciosed
Details_[F0G132 Coton Hand Car Wash T703E Washingion St ANNUAL | 12292015 | 03242015 IPASS; Fio Stop Aulo car wash? Colln Car
Details_|F0G-055 iy Lube 701 E Weshnglon SUR 100|  ANNUAL | 12272015 | 03262015 759
Details_[F0G-090 Siaios TIHE Washinglon St ANNUAL | 12272015 | 03242075 5
Dotails_[FO5012 Gz Cline TEZAE Washingion St ANNUAL | 12272015 | 03242015 5
Details_[FOG017 oan Foll TZ0E. Washingion St ANNURL | 02272015 | 02242075 |AuloS checuled by FOG-17 1 ANNDAL |
Details_[F06-058 EParAllo Sevices 271 East Washiglon Sieel|  ANNUAL | 02272015 | 02262015 AuioS chechled by: FOG-068 | ANNDAL |





Figure 7‑3 Main Screen - FOG Control Program
The inspection will reveal if any bacterial, enzymatic, or chemical agents are used to dissolve, emulsify or suspend FOGs.  The bacterial, enzymatic, or chemical agents may be found in products used for cleaning silverware, pots and pans, drain cleaning, and floor cleaning.  Some products are specifically designed as a grease interceptor additive and are used to liquefy the FOGs in the grease interceptor with the promise that the interceptor will never need pumping.

The site inspection will also evaluate the grease interceptor for performance and integrity.  The City uses the “25% Rule” when determining the efficiency of grease removal by an interceptor.  The 25% Rule simply states that when the operational fluid capacity has been reduced by more than 25%, the interceptor is no longer capable of removing FOG at its designed rate and therefore needs to be serviced.  The performance will also be affected by missing elbows or mid-wall tees or influent extensions that are too long.  The integrity of the interceptor is often affected by anaerobic conditions that generate sulfide gas that causes corrosion of concrete surfaces.  Once the concrete begins to corrode, plumbing connections are compromised and, in some cases, the structural integrity of the interceptor is in question. 

The ECD also works closely with the San Bernardino County Department of Environmental Health to share information gained during restaurant inspections. The ECD inspectors have some knowledge of what constitutes Health and Safety Code restaurant violations.  When these violations are observed, a phone call is placed to the Health Department to have the area inspector respond and take appropriate enforcement actions.
7.4 Public Education and Outreach

The City uses the ECD inspectors as the principle education and outreach method to contact the restaurant community and residents.  Occasionally the ECD inspectors will participate in outreach efforts sponsored by other agencies.  During an inspection of a restaurant, the inspector will use the opportunity to inform and educate the owner or manager about the various laws and regulations that affect their business.  The inspectors also provide useful information (See Section 7.4.1) related to interceptor design, maintenance, and businesses that can assist the restaurants in maintaining pretreatment equipment. Subject areas would include: 

1. Product usage and substitution;

2. Good housekeeping practices;

3. Grease interceptor evaluation;

4. Ordinance O-02-15 legal authority citations; and

5. The City ECD permit requirements.  

The City also has a web site that informs residents about the proper disposal methods for FOG.  Posters and flyers are available instructing residential customers to, “Never pour kitchen grease down the drain” or “put it in a container and dispose of it in the trash.”  This web site educates the resident about the proper care of their sewer lateral and the need to keep FOG out of the sewer.  The residents are encouraged to call to receive more information or clarifications about the care of their sewer laterals. Information for sewer lateral care and FOG are available of the web at http://www.ci.colton.ca.us.

7.4.1 Sample BMP Posters for Food Service Establishments

[image: image37.jpg]GOOD GLEANING PRAGTIGES
Managing ~, L and GREASE

POST IN GLEANUP/ WORK AREA

THE

RIGHT WAY

Wipe pots, pans, Dispose of food Collect waste Clean mats inside

and work areas ﬂ waste directly oil and store over a utility sink.

prior to washing. into the trash. for recycling. Use dry clean up
for spills.

Do not pour Avoid using the Do not pour waste Do not wash floor
cooking residue 2 garbage disposal. 3 oil directly into the mats outside where
directly into Place greasy food drain, parking lot water will run off
the drain. in the trash, or street. directly into the
storm drain.
Do not rinse spills

For more information call (909) 370-6128 or visit www.ci.colton.ca.us into the street.

@ ,?E:;%n:;x;‘f mmwmr—m
g & www.|lacsd.org





[image: image38.jpg]Buenas Practicas de Limpieza
Maneni , AGEITE y GRASA

Mantenga Letrero en el Area de limpieza/Trabajo

FORMA CORRECTA
L

=
T (3 et
e 3 b

s et





Figure 7‑4 Restaurant FOG Posters
Inspectors will provide BMP FOG Posters to each food service establishment and instruct the site managers as to the importance and requirements to implement BMPs.  The posting of FOG Posters is mandatory and failure to implement BMPs will lead to enforcement actions.
7.4.2 Commercial Grease Interceptor Requirements
City of Colton Municipal Code 13.08.235 requires designated food processing facilities, including restaurants to install an approved gravity separation interceptor. The interceptor is required to meet all installation and maintenance requirements of the City of Colton. Interceptors are sized according to the design criteria specified in the current version of the Uniform Plumbing Code.  The interceptor shall contain a minimum of two chambers, with a manhole cover over each chamber, and shall include a sample box. The sample box collects wastewater, which is sampled to verify the compliance with required discharge limits.  City of Colton Municipal Code 13.08.240 requires permitted food service facilities to meet specific discharge limits designed to protect the sewer collection and treatment system. The following information sheet of useful information is provided to businesses upon request. 
[image: image60.jpg]



GREASE MANUFACTURERS, INSTALLERS & HAULERS

The City of Colton does not endorse or otherwise promote any of the businesses listed below.  The list is complied and provided for informational use only.

	Interceptor Manufacturers
	Interceptor Installers
	Grease Waste Haulers

	Pro-Cast Products

(909) 793-7602
	EDCA

(909) 822-5261
	Casey’s Pumping Systems

(909) 884-8288

	
	Arrowhead Septic Tank/Cesspool

(909) 875-8373
	Max Masterson

(909) 820-1620

	Jensen Precast Concrete Products

(909) 350-4111 or (800) 257-6100
	Gosney Construction

(909) 877-0200
	Honeydippers Pumping

(909) 824-3366

	
	Bedlington’s Backhoe Services

(909) 877-4750
	Shields Industries

(800) 244-5899

	Pyramid Precast Company

(909) 823-4255
	Koston Construction

(909) 884-0559
	Integrated Waste Management

(909) 424-1648

	
	Rescue Rooter

(909) 423-0710
	Minuteman Rooter

(800) 628-7867

	Nottingham

(818) 338-1145
	Roto Rooter

(909) 682-1692
	SMC Grease Specialists

(951) 788-6042


Figure 7‑5 Interceptor Manufacturers, Installers, and Grease Haulers
7.5 Plan Check Inspections

The City review wastewater questionnaires and permit applications in addition to plumbing plans to determine the requirements for on-site treatment.  The Uniformed Plumbing Code and grease interceptor sizing criteria are used to determine the capacity requirements for the interceptor  Once plumbing plans are approved the city requires that the builder (proponent) schedules on-site inspection(s) to verify installation of plumbing and interceptor are in compliance with the approved plans.  Figure 7-6 shows a grease interceptor (2,000-gallon capacity) that is ready for inspection of the internal plumbing to ensure compliance with approved specifications.
[image: image39.jpg]



Figure 7‑6 Interceptor Installation Inspection

7.6 Best Management Practices

The City has adopted Best Management Practices related to the operations and maintenance of grease interceptors and in the housekeeping operations associated with food preparation and cleanup at restaurants and other food service type facilities.
BMPs are not just guidelines for food service operations; they are enforceable when a FSE fails to implement one or more of the listed BMPs. The adopted BMPs are as follows:
7.6.1 Food Prep Area BMPs
Introduction:  Fats, Oils and Grease (FOG) are food by-products that can severely damage a facility’s drain line system as well as the sanitary sewer system. FOG collect and eventually harden on the inside of the sewer pipes; preventing water from flowing and causing blockages.
Blockages in the sewer cause Sanitary Sewer Overflows (SSOs), dumping raw sewage into streets, lakes, streams, homes and businesses. The best way to prevent blockages is to keep the FOG out of the drain line system. Below is a list of Best Management Practices that will help to prolong the life of your drain line system and reduce the inconvenience and cost of line blockages.

· Don’t put grease or fryer oil down any sink or floor drain. 

· Don’t dispose of food or food scraps in sinks. 

· Don’t pour bleach directly down ANY drain. Bleach when used improperly dewaters grease, making is as hard as concrete. 

· Don’t take out sink strainers or drain covers. Empty scraps into trash, not down the drain. 

· Don’t use cleaning chemicals improperly. Follow the instructions on the label, for your safety as well as the safety of the environment.

· Scrape all solid food waste into the garbage. 

· Encourage staff to be conservative about use of FOG in food preparation and serving. 

· Use all cleaning chemicals according to the instructions on the label. 

· Use paper towels to soak up oil and grease under fryer baskets and to wipe down work areas. Dispose of the paper towels into the trash. 

· Eliminate the use of garbage disposals.  

· Check all sinks and floor drains for strainers and covers and ensure they are in place and in good working order. 

· Be Knowledgeable regarding the location, operation, and maintenance schedules of all FOG control devices. 

· Ensure that used fryer oil is placed in the appropriate recycling container. 

· Maintain all required grease removal devices (i.e. grease traps or interceptors) in good working order at all times.
7.6.2 Interceptor and Grease Trap Maintenance BMPs
Best management practices for controlling fats, oils, and grease also include maintenance of any required grease removal devices. The approved technology for removing FOG is a gravity interceptor or grease trap (referred to hereafter as treatment unit).  For the treatment unit (TU) to work effectively, it must be cleaned periodically to ensure adequate detention time (the time water remains in the unit before passing through to the sewer).  
Ensuring adequate detention time is accomplished by proper “sizing” when the TU is first installed and secondly by maintaining the TU so that 75% or more of the design capacity is available when in use.  The City inspects grease interceptors on an annual basis (more often if necessary) and evaluates the TU’s condition and the ability to remove FOG. The following BMPs are required for interceptor & grease trap maintenance. 

· Contract an approved grease waste hauler to completely clean all chambers of the interceptor including the sample box (if one exists).
· Establish a routine interceptor cleaning schedule and adjust the schedule based upon condition of interceptor after routine service. A minimum of 75% available capacity must be maintained at all times.
· Observe the interceptor cleaning periodically to ensure the waste hauler is doing a thorough job. This also provides you an opportunity to view the internal plumbing to ensure it is in good working order and complies with City standards.
· Don’t use any emulsify agents in the interceptor that inhibits the interceptor from separating floatables and solids from the final effluent.  

· Keep Records that document all interceptor service events on-site for the City inspector to review. 
7.7 Sewer Line Cleaning and Assessments

The City has approximately 110 miles of gravity draining sewer lines and 4 miles of force main sewer lines.  The majority of the gravity flow lines are 8 inches in diameter.  The contracted sewer maintenance crew is scheduled to clean the entire system each year to sure that the system’s operational capability is realized.  The collection system also has eight (8) sewer lift stations that are inspected on a weekly basis to insure peak performance.
All the attention to line cleaning and lift station performance focuses on system integrity.  A two-inch thick deposit of FOG on the sidewalls of an eight-inch sewer line can lead to an SSO under high flow conditions that the “clean” sewer line could accommodate.  Scheduled inspection and cleaning programs prevent many SSOs from occurring.  Known sewer problem areas are documented and are maintained more frequently.  

The Wastewater Division Staff prepares written reports for all sewer-cleaning activities, including SSOs.  These reports provide the details of the condition of the sewer line and any problems.  When heavy or excessive FOG or other obstructing substances are found, a report is forwarded to the ECD for investigation. The ECD performs on-site inspections at suspected facilities and takes appropriate steps (educational or enforcement actions) to remediate the problem. 
7.8 Sewer and Lateral CCTV Inspections

[image: image61.jpg]



The most useful tool used by the Collection Staff to evaluate the condition of the sewer system is closed circuit television (CCTV) inspection.  The Wastewater Department has one CCTV vehicle that is used as needed to inspect the City’s sanitary sewer and storm drains.  The goal is to have a video library of every sewer line in the City’s service area.  As shown in the photo to the right, grease has begun to build up on the upper wall in two locations of this sewer line and posses a significant threat for creating a blockage in the near future if this line is not service immediately.

The CCTV inspections are also used to provide information about sewer line blockages.  Since these CCTV inspections are recording actual events and conditions, the CCTV records can be used as evidence in an enforcement action.  Sewer and lateral CCTV inspections are a necessary component for the ECD to bring an enforcement action against a business or company that has caused or has the potential to cause a sewer line blockage and/or SSO.

7.9 Enforcement

The discharge of wastewater by a user that causes a sewer line obstruction or blockage is prohibited by the federal Clean Water Act, 40 CFR 403.5(b)(3) and Ordinance O-02-15. The ECD is empowered by the City’s federally approved pretreatment program to take enforcement actions against any user that causes a sewer line obstruction and/or SSO.  In order for the enforcement action(s) to be successful, a firm foundation of court admissible evidence must be obtained.  This evidence must be objective and devoid of personal opinions.  The use of CCTV evidence is a critical component of an enforcement action taken against a user for causing a sewer line blockage and/or SSO.  In addition to the CCTV evidence, inspections are performed by the ECD at the suspected business to evaluate and investigate the cause(s) of the sewer line blockages and/or SSO.  Once all the evidence is collected, the information is reviewed and an enforcement strategy is developed using the City’s approved Enforcement Response Plan (ERP).  

The level of initial enforcement will always be commensurate with the severity or chronic nature of the violation.  If the sewer-line debris accumulation has just begun and no SSO or sewer obstruction has occurred, then a correction notice may be issued to improve housekeeping practices and evaluate the business practices that may lead to the discharge of materials that caused the sewer-line debris accumulations.  If the sewer-line debris accumulations are significant and/or an SSO has occurred, then more severe enforcement actions may be taken.  A Notice of Violation (NOV) or a Cease and Desist Order (CDO) may be issued with a compliance schedule to mitigate the conditions that caused the sewer line blockage and/or SSO to occur.   The NOV or CDO will require that the discharges causing the sewer line blockage and/or SSO must stop immediately and the user shall take all actions necessary to prevent any future discharges that would cause a sewer- line blockage or SSO.  Corrective action reports must be submitted in writing and the user is held accountable for effective and timely implementation.  If the user fails to achieve compliance or is unresponsive to the requirements of the correction orders, then additional civil and/or criminal actions may be taken.

Ordinance O-02-15 Section 13.08.253 C prohibits the use of any chemical or material that will emulsify, suspend or dissolve oil and grease and the use of any microbiological product to metabolize FOG.  The ECD inspection staff is constantly looking for these products during every restaurant inspection.  When a prohibited product is discovered being used, the user is ordered to immediately stop the use of the product and have the product removed from the premises.  Failure to comply with these administrative orders may result in additional enforcement actions, including civil and/or criminal actions.

7.10 Grease Interceptor Retro Fits

One of the primary grease reduction strategies used by the City is the requirement for FSEs to install approved grease interceptors.  For new construction and tenant improvement projects, interceptor requirements are determined during the City’s plan check process.  Building permits cannot be obtained if the user has not agreed to the ECD requirements for the project.  
If an existing food service establishment is determined to be the cause or a contributor to a grease related sewer line blockage and does not have an approved interceptor, the following process is used.

· A BMP Brochure and/or Poster is delivered and explained during an on-site inspection.

· The inspection form will clearly state the grease issue and that BMPs must be instituted immediately to determine if the grease loading can be reduced sufficiently through BMP practices alone.

· If grease problems continue (either because the utilization of BMPs alone were not sufficient or if BMPs were not implemented), the user will be issued a Notice of Violation with a compliance schedule for installing the required interceptor equipment. 
The process detailed above also applies to existing food service establishments that have a grease interceptor but the device is not properly maintained or is inadequate (under sized for the flow volume) to treat the type and volume of wastewater from the facility. 
Any restaurant or similar facility found responsible for the sewer line blockage and/or SSO, will be assessed all costs of cleanup and/or repairs necessary to remove the blockage and/or SSO. 
7.11 Training

The ECD inspector has knowledge, skills, and abilities that are constantly being challenged and improved.  Training of the inspector for FOG issues is 
critical to insure that the inspector is adequately equipped to respond to restaurant inspection and SSO investigation findings.  This training includes:

1. Laws and regulations;

2. Cleaning, degreasing, and microbiological product identification and use;

3. New technology and equipment;

4. New pretreatment methodology;

5. Inspection practices; and

6. Enforcement actions

The City’s ECD inspectors have received training from the following sources: 

1. Pretreatment training;

2. Specialty conferences and events;

3. Special schools and training events; and

4. On the Job Training (includes meetings, discussions, and field training with more experienced ECD inspectors).

7.12 FOG Control Program Summary

The City’s ECD and Collection System Section work closely to identify, investigate, and correct problems caused by the discharge of FOG to the City’s sewer system. Preventive rather than reactive sewer inspection and cleaning combined with food service establishment (FSE) inspections are critical to insure the integrity of the City’s collection system.  Prompt responses to SSOs are necessary to mitigate the effects to the SSO in a 
timely manner.  The City’s ECD also work closely with the County Public Health Department to expedite corrective actions by the FSE.  

In extreme cases, the City may enlist the services and resources of the Californian Regional Board Water Quality Control Board to provide additional incentive for correcting water quality and public health concerns. 
Our goal is to reduce FOG related incidents each year and to eliminate all FOG related SSO’s within 3 years.
7.13 Roles and Responsibilities

The City’s ECD is responsible for implementing the provision described in the FOG Control Program.  Additionally, the ECD will review and update the FOG Source Control Program and Enforcement Management System documentation, as the need arises.
8.0 SYSTEM EVALUATION AND CAPACITY ASSURANCE PLAN
8.1 Introduction
Wastewater Master Plan Update is currently 60% complete (prepared by Corollo Engineers). The estimated time of completion is December 2015.  A complete copy of the previous Master Plan is included as Appendix G of the SSMP. While the data contained in this document is more than ten (10) years old, much of the data is still relevant and useful in decisions regarding capacity assurance and system reliability.  
One of the findings contained in the Master Plan concluded that a significant portion of the City’s sewer collection system infrastructure was constructed around 1910 and that an estimated $1.7M per year over the next ninety years would be needed to assure system reliability.  The City has increased line maintenance, CCTV activities, lift station maintenance, and other predictive and preventative maintenance steps to improve system reliability until funding is available for additional capital improvements. The capital (connection) fees remain at $6/gallon as adopted in 1996.  The City is re-evaluating the connection fee, which is significantly lower than other cities in the region. 
8.2 Evaluation
The portions of the collection system, which are vulnerable to an SSO due to hydraulic deficiency, are identified in the Wastewater Master Plan. Included in the evaluation are estimates of peak flows (including from SSO’s that escape from the system) associated with conditions similar to those causing overflow events, estimates of the capacity of key system components, hydraulic deficiencies (including components of the system with limiting capacity), and the major sources that contribute to the peak flows associated with overflow events.
8.3 Design Criteria

Facility design criteria fall into one of the following wastewater facility components:

· Conveyance Facilities

· Wastewater Treatment Facilities

The conveyance facility design criteria are discussed in detail in the 1997 Master Plan, by Kennedy/Jenks. The treatment facility component is detailed in a previous study completed in 1995.  
8.4 Capacity Enhancement Measures

The City has established a short- and long-term capital improvement program (CIP) to address identified hydraulic deficiencies. The CIP includes project cost estimates, project prioritization, alternatives analysis, and construction schedules. 
8.5 Plan Updates and Schedules:

The CIP review occurs during the budget process. The review identifies any significant changes in proposed actions and/or implementation schedules, and some of the indicators of performance from the SSMP may serve as justifications for future expenditures. Sewer rates are evaluated and adjusted periodically. The latest update to the sewer rates was in 2014.

The City has design standards and guidelines to ensure adequate capacity. The City relies on the most recent Wastewater Master Plan, updated information received from City and contracted personnel from actual observations of wastewater flows seen at locations throughout the City; and documented capacity issues detected during the previous 12 months. These programs are described in more detail in the Wastewater Master Plan (Appendix G). 

The City Water & Wastewater Department Director prepares annual and long-term goals that include wastewater capacity assurance.  The City is not currently experiencing capacity-related problems. The Wastewater Department communicates potential or emerging capacity problems to City management for consideration in upcoming capital projects. 
8.6 Monitoring Capacity Assurance and System Performance
The City utilizes numerous data sources, daily observations, and regulatory reports in determining the performance of the wastewater collection and treatment system. Some of the data sources and reports are listed below.
· Wastewater Master Plan; 

· Monthly SSO Report;

· Operations and Maintenance Annual Report;

· Quarterly and Annual Pretreatment Reports; 

· The City’s Capital Improvement Program; 
· Daily Wastewater Cleaning Reports; and

· CCTV records
8.7 Roles and Responsibilities

The City reviews CIP monies and priorities annually during the budget process.  The Public Works Director provides justifications and specific details based upon a variety of dynamic factors and established priorities for maintaining the wastewater collection system and treatment plant infrastructure. The City Manager, Finance Director, and ultimately the city council must sign off on major capital projects before work begins.
A copy of the 9-year CIP, developed in FY2014-15, is shown on the following page.


[image: image40.emf]Project Description 2015 2016 2017 2018 2019 2020 2021 2022 2023 Project Cost

Wastewater Treatment Plant Capacity and Infrastructure Upgrade

Asphalt Paving of Existing Utility Easement 

207,200 $      - $                   - $                   - $                   - $                      - $                      - $                      - $                      - $                      207,200 $        

Centrifuge Project 

1,346,800 $  - $                   - $                   - $                   - $                      - $                      - $                      - $                      - $                      1,346,800 $    

Center Street Lift Station Project

- $                   - $                   555,967 $     575,982 $     2,983,588 $     - $                      - $                      - $                      - $                      4,115,537 $    

36-inch Sewer Main at Rancho and Lift Station

- $                   555,967 $     1,075,982 $  1,596,718 $  - $                      - $                      - $                      - $                      3,228,667 $    

Construction of Administration and Control Building (5,000 SF)

- $                   - $                   - $                   - $                   - $                      1,327,022 $     1,374,795 $     - $                      - $                      2,701,816 $    

Upgrade of Electrical System (switch gear & service conversion to VFD)

- $                   - $                   778,354 $     - $                   - $                      - $                      - $                      - $                      - $                      778,354 $        

Upgrade Digester No. 3 (Install Methane Filtration & Cleaning System)

- $                   - $                   444,774 $     - $                   - $                      - $                      - $                      - $                      - $                      444,774 $        

Install Aeration Basin No. 6 and Secondary Clarifier No. 6

- $                   - $                   - $                   - $                   - $                      - $                      - $                      1,990,533 $     2,062,192 $     4,052,724 $    

Removal and Disposal of Claraetor and Clarifier

- $                   - $                   - $                   345,589 $     - $                      - $                      - $                      - $                      - $                      345,589 $        

Removal and Disposal of Digester No. 1

- $                   - $                   - $                   - $                   238,687 $        - $                      - $                      - $                      - $                      238,687 $        

Upgrade Headworks and Install Bar Screen

- $                   - $                   - $                   57,598 $       59,672 $          123,640 $        - $                      - $                      - $                      240,910 $        

Upgrade Digester No. 2 with New Floating Dome

- $                   751,307 $     - $                   - $                   - $                      - $                      - $                      - $                      - $                      751,307 $        

Construction of Digester

- $                   - $                   - $                   - $                   - $                      - $                      - $                      1,327,022 $     1,374,795 $     2,701,816 $    

Enlargement of Chlorine Contact Lagoon

- $                   - $                   - $                   - $                   - $                      - $                      - $                      - $                      274,959 $        274,959 $        

Wastewater Collection CIP

La Cadena Sewer Line

290,080 $      - $                   - $                   - $                   - $                      - $                      - $                      - $                      - $                      290,080 $        

Sewer Line Replacement

- $                   300,000 $     300,000 $     300,000 $     300,000 $        300,000 $        300,000 $        300,000 $        300,000 $        2,400,000 $    

Center Street Sewer Line and Lift Station

- $                   - $                   - $                   - $                   1,000,000 $     1,500,000 $     1,500,000 $     4,000,000 $    

Total= 1,844,080 $  1,607,275 $  3,155,078 $  2,875,887 $  4,581,946 $     3,250,662 $     3,174,795 $     3,617,554 $     4,011,945 $    

Total Commulative= 1,844,080 $  3,451,355 $  6,606,432 $  9,482,319 $  14,064,266 $  17,314,927 $  20,489,722 $  24,107,276 $  28,119,221 $ 

Note:

Added $1.5M for the construction of Lift Station 

Added $2.4M for Sewer Replacement Project

Added $4M for center Street Sewer and Lift Station

Added $0.5M for 2017 and $1M for 2018

COLTON WATER FACILITIES

CIP PROJECT SCHEDULE



9.0 MONITORING, MEASUREMENT, AND PLAN MODIFICATIONS
This section addresses SSMP provisions outlined in Section D, 13 (ix) Monitoring, Measurement, and Program Modifications of SWRCB Order No. 2006-0003. 

The City Monitoring, Measurement, and program Modifications encompass the following components:

· Maintain relevant information that can be used to establish and prioritize appropriate SSMP activities;

· Monitor the implementation and where appropriate, measure the effectiveness of each element of the SSMP;

· Asses the success of the preventive maintenance program;

· Update program elements, as appropriate, based on monitoring or performance evaluations; and
· Identify and illustrate SSO trends, including frequency, location, and volume.
9.1 Performance Measures

The indicators that the City will use to measure the performance of its wastewater collection system and the effectiveness of its SSMP are:
· Total number of SSOs;

· Number of SSOs by each cause (roots, grease, debris, pipe failure, capacity, pump station failures, and other)

· Portion of sewage contained compared to total volume spilled;

· The total volume of spilled sewage discharged to surface water;

· Scheduled vs. actual performed preventive maintenance (i.e., miles of collection system cleaned, lift station maintenance, etc.) tasks; and
· Property damage claims

9.2 Baseline Performance

The City has limited historical, or baseline, performance data for the selected performance measures since this is an emerging requirement. Performance goals and trends established during the first full year of the program will provide the baseline for measuring future performance. In general, the City will strive to better baseline numbers as an indicator of performance however there may be instances when baseline numbers are determined to be indicators of time spent completing tasks that are not as critical to overall performance as other areas.  For example, the baseline for “miles of sewer line cleaned” may be “the entire system annually”.  It may be determined that some areas don’t require annual cleaning and that a better use of the time may be spent videoing portions of the system or devoting more cleaning time to problematic areas. The total reportable SSOs is clearly a valuable indicator and the City will strive to decrease the number of overflow occurrences; the volume of SSO discharges; and the damages to private property that result from SSOs.
9.3 Performance Monitoring and Program Changes

The City will evaluate the performance of its wastewater collection system at least annually using the performance measures identified in Subsection 9.1, Performance Measures.  The City will update the data and analysis at the time of the evaluation.

The City may use other performance measures in its evaluation. The City will prioritize its actions and initiate changes (updates) to the SSMP and the related programs based on the results of the evaluation.
10.0 SSMP PROGRAM AUDITS

This section addresses the SSMP provision required in section D, 13 (x) SSMP Program Audits of SWRCB order No. 2006-0003.

The City is required to conduct periodic internal audits, appropriate to the size of the system and the number of SSOs. At a minimum, these audits must occur every two years and a report must be prepared and kept on file. This section outlines the process that the City will follow to evaluate the effectiveness of the SSMP to identify opportunities for program modifications that increase the operational sustainability of the wastewater collection system. 
10.1 Audits

The use of program audits is a valuable tool to assess performance. The information collected during the audit process is valuable for ensuring continuous improvement to the SSMP. 

The scope of the audits will include a review of each major element of the SSMP and the corresponding achievements. The audit will include, but is not limited to, a review of the year to date (YTD) goals for line cleaning; video inspections; the timeliness of response to service requests and other work orders; effectiveness of the SSO responses including mitigation, clean-up, reporting, and property damage.  

The City’s Wastewater Department will perform a self-audit or contract a third party audit to ensure continuous improvement and effectiveness in achieving the stated goals and objectives. 
10.2 SSMP Updates

The City will determine the need to update its SSMP based on the results of the audit and the performance of its wastewater collection system. The City will develop a process for updating the SSMP when necessary to achieve a stated goal or objective. The City will complete the update within one year of completion of the audit.  
10.3 Annual Goals

The annual audit will focus on accomplishing the following stated goals:

A. To minimize the frequencies and magnitude of SSO’s in the City;
B. To optimize the operation and maintenance of the City’s collection system;
C. To provide notifications and reports to all required regulatory agencies in a timely manner;
D. To mitigate the effects of any SSO that may occur; and
E. To increase public awareness of FOG issues and how they can affect the collection system.
10.4 Roles and Responsibilities

An individual or team, as assigned by the Public Works Director, will conduct the SSMP audits using the checklist as shown in Table 10-1.

10.5 SSMP Audit Categories
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	

	
	
	
	
	
	
	




As specified in the Order, the SSMP is comprised of eleven (11) elements or subsets of Section D.13 of the Order, as follows: 

[image: image62.jpg]L

12 N
WHEN._SUBJECT|
7O TRAFFIC

24 CAST IRON FRAME
& COVER WITH GASKET
(GASTIGHT), 3 STANDARD

2=

4 PVC INLET)
QUTLET PIPE

e
Coltes o
0),





	Element No
	Reference Section
	Heading

	1
	D.13.i
	Goals

	2
	D.13.ii
	Organization

	3
	D.13.iii
	Legal Authority

	4
	D.13.iv
	Operation and Maintenance Provisions

	5
	D.13.v
	Design and performance Provisions

	6
	D.13.vi
	Overflow Emergency Response Plan

	7
	D.13.vii
	FOG (fats, oils, grease) Control Plan

	8
	D.13.viii
	System Evaluation and Capacity Assurance Plan

	9
	D.13.ix
	Monitoring, Measurement and Program Modifications

	10
	D.13.x
	SSMP Program Audits

	11
	D.13.xi
	Communication Program


 Table 10‑1 SSMP Audit Categories

This internal audit is focused on the above eleven categories as required by the Order.  The evaluation of each element in each category is herewith standardized with effectiveness, the measure of audit evidence obtained from City staff.  Compliance ranking has been based on Order audit guidelines and effectiveness.  A recommendation has been provided when there is enough information to support it. 

The format for audit reporting is as follows: 

· Order Section/Subsection 

· Effectiveness Ranking  

· Complies,  

· Substantial Compliance,  

· Partial Compliance,  

· Marginal Compliance, and  

· Not in Compliance 

· Findings 

· Reference Information 

· Recommendation when appropriate  

11.0 COMMUNICATION PROGRAM

This section addresses the SSMP provision outlined in Section D, 13 (xi) Communication program of SWRCB Order No.2006-0003.

The City has several means to communicate the elements of the SSMP to the public. These are through direct mailings, the City’s website, personal contact by collection crew and Pretreatment Program and the City’s call center.

11.1 Direct Mailings, Counter Brochures and Internal Memos
The City utilizes utility billing inserts and brochures for communicating with the residential and commercial customers on a wide range of topics including SSOs and managing Fats, Oils, and Grease. Many of these brochures are also available at the City’s Corporate Yard and at City Hall. The City’s Water & Wastewater Department also generates and distributes memos to other departments (e.g., reminders about City policies for removing manhole covers during storm events, etc.) to help reduce the number of preventable SSOs. 
Residents and Commercial customers are encouraged to participate in all City Programs through a variety of media including televised City Council Meetings, updated and interactive City web site, and workshops. 
11.2 City Web Site

The City’s web site (www.ci.colton.ca.us) includes SSO and FOG Control Program requirements and associated documents. The City website provides general and detailed information about how the City responds to SSOs and the programs that are in place to prevent SSOs.  Specific documents (e.g., SSMP, Ordinance, Enforcement Response Plan, and the Fats, Oil, and Grease (FOG) program) are available on the web site in PDF versions.  The City accepts comments for all information posted on the City’s website.  
11.3 Personal Contact

Colton’s Wastewater & Collection System personnel respond to all SSO’s and are the first means of communication regarding prevention of SSO’s and preventive maintenance.  If a SSO is caused by a blockage in a private lateral, the private lateral sewer policy is explained and distributed to the customer. The City also provides information regarding appropriate corrective actions.  The customer is instructed to call a private plumber to make the necessary repairs or corrections. As a courtesy, City crews will clean the sewer line that services the area to ensure that there are no obstructions causing the private lateral problem.

The City’s Environmental Compliance Section interacts with the commercial and industrial businesses, including restaurants. Inspections are conducted at restaurants to ensure that grease interceptors, sewer laterals, and outdoor areas are properly maintained. The inspectors use the inspection as an opportunity to communicate laws, regulations, and policies that affect the industry or commercial business. These laws include the FOG program, NPDES Storm Water Permit requirements, the SSMP, and good housekeeping practices. The inspectors deliver program information in the form of brochures and other printed material, in English and Spanish. Other version (e.g., Korean, Chinese, and Japanese) are available upon request.
11.4 City’s Call Center

The City’s main line (909-370-5000) allows the residents of Colton’s service area to report problems related to any City services.  Calls are routed according to established procedures to the proper City and/or contracted services to respond in a timely manner. 
12.0 SSMP COMPLETION AND CERTIFICATION

The City of Colton’s City Council has reviewed and approved the City’s SSMP.  The Public Works Director will certify this adoption and notify the State of California Water Resources Control Board through the electronic certification format provided in the CIWQS reporting system.  

13.0 APPENDICES
Appendix A – Regulatory Permits

A-1 
Statewide General Waste Discharge Requirements (GWDR)

A-2 
GWDR Monitoring & Reporting Program

A-3 
Amended GWDR

A-4 
San Bernardino County Flood Control MS4 Permit
Appendix B – Notice of Intent
Appendix C – Sewer Use Ordinance Number O-02-15
Appendix D – City of Colton Enforcement Response Plan
Appendix E – City of Colton Sewer Standards
Appendix F – Private Lateral Sewer Policy
Appendix G – City of Colton Wastewater Master Plan
Appendix H – Capital Improvement Plan (CIP)
APPENDIX A – REGULATORY PERMITS

APPENDIX A-1 

STATEWIDE GENERAL WASTE DISCHARGE REQUIREMENTS FOR SANITARY SEWER SYSTEMS

State Water Resources Control Board Order No. 2006-0003

APPENDIX A-2 

MONITORING & REPORTING PROGRAM (MRP)

State Water Resources Control Board Order No. 2006-0003

APPENDIX A-3 

AMENDED STATEWIDE GENERAL WASTE DISCHARGE REQUIREMENTS FOR SANITARY SEWER SYSTEMS

State Water Resources Control Board Order No. WQO 2008-0002 EXEC

APPENDIX A-4 

SAN BERNARDINO COUNTY FLOOD CONTROL MUNICIPAL SEPARATE STORM SEWER SYSTEM (MS4) PERMIT
State Water Resources Control Board Order NO. R8-2002-0012
APPENDIX B 

CITY OF COLTON – NOTICE OF INTENT
APPENDIX C 

CITY OF COLTON WASTEWATER RULES AND REGULATIONS
ORDINANCE NO. O-02-15
MUNICIPAL CODE SECTION 13.08

APPENDIX D 

CITY OF COLTON ENFORCEMENT RESPONSE PLAN (ERP)
APPENDIX E 

CITY OF COLTON 

WASTEWATER SYSTEM STANDARD DRAWINGS
APPENDIX F 

CITY OF COLTON
PROGRAM FORMS
APPENDIX G 

WASTEWATER SYSTEM MASTER PLAN
Kennedy/Jenks, October 1997

APPENDIX H 

CITY OF COLTON

CAPITAL IMPROVEMENT PLAN (CIP)
APPENDIX I 

SEWER LATERAL POLICY
Ordinance O-02-14
Sewer System Management Plan (SSMP)





City of Colton


Water Reclamation Facility


1201 S. Rancho Dr. 


Colton, CA 92324


(909) 370-6128








2015 Revision





Figure � STYLEREF 1 \s �7��� SEQ Figure \* ARABIC \s 1 �2� Plugged Interceptor





Figure � STYLEREF 1 \s �7��� SEQ Figure \* ARABIC \s 1 �7� Grease Buildup – Sewer Main

















[image: image63.jpg]ENVIRONMENTAL
COMPLIANCE, INC.

pr =




City of Colton SSMP
III
2015


[image: image64.png]


_1482211886.unknown

_1482211888.unknown

_1482211889.unknown

Sheet1

				COLTON WATER FACILITIES

				CIP PROJECT SCHEDULE



						Project Description		2015		2016		2017		2018		2019		2020		2021		2022		2023		Project Cost

						Wastewater Treatment Plant Capacity and Infrastructure Upgrade

						Asphalt Paving of Existing Utility Easement 		$   207,200		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   207,200

						Centrifuge Project 		$   1,346,800		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   1,346,800

						Center Street Lift Station Project		$   -		$   -		$   555,967		$   575,982		$   2,983,588		$   -		$   -		$   -		$   -		$   4,115,537

						36-inch Sewer Main at Rancho and Lift Station		$   -		$   555,967		$   1,075,982		$   1,596,718				$   -		$   -		$   -		$   -		$   3,228,667

						Construction of Administration and Control Building (5,000 SF)		$   -		$   -		$   -		$   -		$   -		$   1,327,022		$   1,374,795		$   -		$   -		$   2,701,816

						Upgrade of Electrical System (switch gear & service conversion to VFD)		$   -		$   -		$   778,354		$   -		$   -		$   -		$   -		$   -		$   -		$   778,354

						Upgrade Digester No. 3 (Install Methane Filtration & Cleaning System)		$   -		$   -		$   444,774		$   -		$   -		$   -		$   -		$   -		$   -		$   444,774

						Install Aeration Basin No. 6 and Secondary Clarifier No. 6		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   1,990,533		$   2,062,192		$   4,052,724

						Removal and Disposal of Claraetor and Clarifier		$   -		$   -		$   -		$   345,589		$   -		$   -		$   -		$   -		$   -		$   345,589

						Removal and Disposal of Digester No. 1		$   -		$   -		$   -		$   -		$   238,687		$   -		$   -		$   -		$   -		$   238,687

						Upgrade Headworks and Install Bar Screen		$   -		$   -		$   -		$   57,598		$   59,672		$   123,640		$   -		$   -		$   -		$   240,910

						Upgrade Digester No. 2 with New Floating Dome		$   -		$   751,307		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   751,307

						Construction of Digester		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   1,327,022		$   1,374,795		$   2,701,816

						Enlargement of Chlorine Contact Lagoon		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   274,959		$   274,959

						Wastewater Collection CIP

						La Cadena Sewer Line		$   290,080		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   -		$   290,080

						Sewer Line Replacement		$   -		$   300,000		$   300,000		$   300,000		$   300,000		$   300,000		$   300,000		$   300,000		$   300,000		$   2,400,000

						Center Street Sewer Line and Lift Station		$   -		$   -		$   -		$   -		$   1,000,000		$   1,500,000		$   1,500,000						$   4,000,000



						Total=		$   1,844,080		$   1,607,275		$   3,155,078		$   2,875,887		$   4,581,946		$   3,250,662		$   3,174,795		$   3,617,554		$   4,011,945

						Total Commulative=		$   1,844,080		$   3,451,355		$   6,606,432		$   9,482,319		$   14,064,266		$   17,314,927		$   20,489,722		$   24,107,276		$   28,119,221

						Note:

						Added $1.5M for the construction of Lift Station 

						Added $2.4M for Sewer Replacement Project

						Added $4M for center Street Sewer and Lift Station

						Added $0.5M for 2017 and $1M for 2018






_1482211887.unknown

_1482211476.unknown

_1482211885.unknown

_1482211477.unknown

_1482211475.unknown

_1303039307.vsd
�

�

�

�

�

FLOW CHART
SANITARY SEWER OVERFLOW RESPONSE PLAN�

SPILL OCCURS/REPORTED DURING REGULAR WORK HOURS�

SPILL OCCURS/REPORTED DURING NIGHTS AND WEEKENDS�

Report of Spill Received by Water - Wastewater Department�

Public�

Other Source�

Wastewater Treatment Plant Manager or Lead Operator Directs the Response Team to Investigate the Spill Call�

SSO Report Form�

Response Team Assess and Categorizes SSO 
(Responds in Accordance with Established Written Procedures)�

�

Sanitary 
Spill?�

Yes�

Category 1 Spill?�

No�

Private Lateral Spill?�

No�

Yes�

Determine Cause & Mitigate
(Contain Spill, Secure Area with Barriers & Signs, 
Prepare Incident/Spill Report
Clean-Up & Disinfect Area)�

Communicates Spill Information�

Data Input into CIWQS System�

Category 2 Spill�

Initial Notification 
to OES, SB County Health, and RWQCB within 2 hours of spill awareness �

Certification to RWQCB 
as soon as possible (but no later than 24-hours) �

Did Spill 
Reach a Drainage Channel or Surface Water? �

Yes�

�

Within 30-Days�

Yes�

Certified e-Report Submitted�

Provide Information Regarding Responsibility for Maintaining Lateral and Assist as Needed to Minimize Public Health Risks�

Initial Report within 3-Business Days
Final Certified Report within 15-Days�

Voluntary�

�

SSO Resolved?�

No�

Yes�

End of Action - File Report(s)�

Notify Manager�

Elevate Response to City Government Level Necessary to Protect Health, Welfare, & Resources as Directed�

Report of Spill Received by City PD Dispatcher�

No�

On-Call Wastewater Staff Notified�

Evaluates 
Information Received & Responds to 
the Site�

No�

Notify Manager, File Report, End Response�

Yes�

Collect Water Samples 
as Determined by RWQCB�


